## Reference
Collector Substation Relay Settings
Project Data
Project | Grover Hill Wind
Client | White Construction/AEP/Lotus
Engineer | T. Clark
Date | 2025-10-03
Revision | A
Shared Settings
Terminal/Station ID | GRVR HL WND
Company Name | AEP
UTC Offset | -5
Default Router | 172.31.100.254
Subnet Mask | 255.255.255.0
DNP Client IP 1 | 172.31.100.241
DNP Client IP 2 | 172.31.100.243
PMU Client IP | 172.31.100.38
Change Log
Revision | Date | Description
A | 2025-10-03 | Issued for Review

## HV_351S
SEL-351S HV Protection Settings & Logic
Relay Specification
Manufacturer | SEL
Model | SEL-351S
Part # | 0351S7XHD3E5441
Function | HV Protection and Bkr Control
Front View |  |  |  | Rear View
Relay Classification
Relay ID (RID) | Setpoint Class | Logic Class | IP Address (IPADDR)
11T1 | A | 1 | 172.31.100.80
I/O Summary |  |  | Remote Bit Summary
I/O | Description |  | Element | Description | Behavior
IN101 | 52T1 Status (a) |  | OC | 52T SCADA Open | Pulse
IN102 | 52T1 Status (b) |  | CC | 52T SCADA Close | Pulse
IN103 | Not Used |  | RB1 | Target Reset | Pulse
IN104 | Not Used |  | RB2 | 89L1 SCADA Open | Pulse
IN105 | 86BFH1 Status |  | RB3 | 89L1 SCADA Close | Pulse
IN106 | 86BFH1 Trip Coil Monitor
OUT101 | 52T1 Protection Trip (TC1)
OUT102 | 52T1 SCADA Trip |  | Pushbutton Summary
OUT103 | 52T1 SCADA Close |  | Element | Description | Target LED
OUT104 | 86BFH1 Lockout Trip |  | PB1 | Remote Enable | LED1
OUT105 | 11T1 Fault Indicator |  | PB2 | Undervoltage Disable | LED2
OUT106 | 52T1 Secondary Trip (TC2) |  | PB3 | Breaker Failure Disable | LED3
OUT107 | 52T1 Block Close |  | PB4 | Not Used | LED4
ALARM | Relay Fail Alarm to DPAC |  | PB5 | Operator Lock (hold for 3 sec) | LED5
IN201 | 52T1 Breaker Failure Initiate |  | PB6 | Trip Coil Failed (push to reset) | LED6
IN202 | 89L1 Status (a) |  | PB7 | Not Used | LED7
IN203 | 89L1 L/R Status |  | PB8 | Not Used | LED8
IN204 | 52T1 Loss of Motor DC |  | PB9 | Not Used | LED9
IN205 | 52T1 Auto Transfer Motor Power |  | PB10 | Not Used | LED10
IN206 | Not Used
IN207 | 52T1 Spring Alarm
IN208 | 52T1 TCM Trip 1 |  | Ratios & Nominal Voltages
IN209 | 52T1 TCM Trip 2 |  | Element | Value
IN210 | 52T1 Low SF6 LO Trip 1 |  | CT Ratio | 240
IN211 | 52T1 Low SF6 LO Trip 2 |  | PT Ratio | 1200
IN212 | 52T1 Low SF6 Alarm |  | HV Bus Voltage (kV LL) | 138
IN213 | Not Used |  | Relay Nominal Voltage (V-sec LN) | 66.4
IN214 | 52T1 74 DC Close
IN215 | 52T1 74 DC Trip 1
IN216 | 52T1 74 DC Trip 2
OUT201 | BF Transfer Trip to 87LP
OUT202 | BF Transfer Trip to 87LS
OUT203 | 89L1 SCADA Open
OUT204 | 89L1 SCADA Close
Short Circuit Current Magnitudes
Setpoint Class | 3PH (A-pri) |  |  | SLG/2PH-G 3I0 (A-pri)
| POI | HV Sub Bus | MV Sub Bus | POI | HV Sub Bus | MV Sub Bus
A | 1407 | 6820 | 2961 | 2523 | 3649 | 555
PH OC Settings |  | Setpoint Class
Level 1 (OFF) |  | A | B | C | D | E
Pickup | 50P1P (A-sec) | OFF
Delay | 67P1D (cyc) | 0
Torque Control | 67P1TC | 1
PH OC Philosophy
Disabled
PH TOC Settings |  | Setpoint Class
Level 1 |  | A | B | C | D | E
Aggegate MVA | MVA | 166.6367
HV Voltage | kV-LL | 138
PRC-025-2, Op. 11 Loadability | A-pri | 906.3047
Pickup | 51P1P (A-sec) | 3.78
Curve | 51P1C | U3
Time Dial | 51P1TD | 1
Torque Control | 51P1TC | 1
PH TOC Philosophy
Set pickup per PRC-025-2, Option 11. Set curve and time dial to coordinate with downstream protection. Set minimum response time to ensure element does not operate before the instantaneous element. Level 1 TOC element must ride through aggregate GSU inrush. PRC-025-2, Option 11 Setting Criteria: The overcurrent element shall be set greater than 130% of the calculated current derived from the maximum aggregate nameplate MVA output at rated power factor (including the Mvar output of any static or dynamic reactive power devices). Where applicable, these elements are set to coincide with downstream transformer HV terminal time overcurrent elements.
GND OC Settings |  | Setpoint Class
Level 1 (OFF) |  | A | B | C | D | E
Pickup | 50G1P (A-sec) | OFF
Delay | 67G1D (cyc) | 0
Torque Control | 67G1TC | 1
GND OC Philosophy
Disabled
GND TOC Settings |  | Setpoint Class
Level 1 |  | A | B | C | D | E
Pickup | 51G1P (A-sec) | 1.25
Curve | 51G1C (cyc) | U3
Time Dial | 51G1TD | 1
Torque Control | 51G1TC | 1
GND TOC Philosophy
Ground time overcurrent settings are set to coincide with downstream tranformer HV terminal time overcurrent elements.
BF Settings |  | Setpoint Class
Level 1 |  | A | B | C | D | E
Pickup | 50BFP (A-sec) | 1.89
Time Delay | BFPU (cyc) | 9
BF Philosophy
Set breaker failure detection pickup to 50% of phase time overcurrent pickup.
Voltage & Frequency Settings
Description | Pickup |  |  | Logic | Pickup Delay
| Element | Setting Value | Per Unit Value |  | Seconds | Cycles
Freq Undervolt Block | 27B81P (V) | 44.488 | 0.67
Level 1 Underfreq | 81D1P (Hz) | 56 | NA |  | 70 | 3920
Level 1 Overfreq | 81D2P (Hz) | 64 | NA |  | 70 | 4480
Level 1 Undervolt | 27P1P (V) | 51.128 | 0.77 | SV6 | 12 | 720
Level 2 Undervolt | 27P2P (V) | OFF | OFF | SV7 | 0 | 0
Level 1 Overvolt | 59P1P (V) | 86.32 | 1.3 | SV8 | 1 | 60
Level 2 Overvolt | 59P2P (V) | 82.336 | 1.24 | SV9 | 3 | 180
Voltage & Frequency Philosophy
Set to comply with PRC-029-1 and to coordinate with HV and Collector voltage and frequency protection. See PRC-029-1 Appendix for coordination curve.
Settings Table
Setting | Value | Description | Category | Function | Setpoint Class | Logic Class | Float | QuickSet Group | SER
PTCONN | WYE | Phase PT Connection | Global | General |  |  | FALSE |  | FALSE
NFREQ | 60 | Nominal Frequency (Hz) | Global | General |  |  | FALSE |  | FALSE
PHROT | ABC | Phase Rotation | Global | General |  |  | FALSE |  | FALSE
LER | 60 | Length of Event Report (cyc) | Global | General |  |  | FALSE |  | FALSE
PRE | 15 | Cycle Length of Prefault in Event Report (cyc) | Global | General |  |  | FALSE |  | FALSE
UTC_OFF | -5 | UTC Offset to Local Time | Global | Time |  |  | TRUE |  | FALSE
BOOPTCC | PULSE | DNP BO Close/Trip Behavior | Global | DNP |  |  | FALSE |  | FALSE
BOOPPUL | PULSE | DNP BO Pulse On Behavior | Global | DNP |  |  | FALSE |  | FALSE
TID | GRVR HL WND | Terminal Identifier | General | ID |  |  | FALSE |  | FALSE
CTR | 240 | Phase CT Ratio (IA, IB, IC) | General | Ratio |  |  | FALSE |  | FALSE
CTRN | 240 | Neutral CT Ratio (IN) | General | Ratio |  |  | FALSE |  | FALSE
PTR | 1200 | Phase PT Ratio (VA, VB, VC) | General | Ratio |  |  | TRUE |  | FALSE
VNOM | 66.4 | Phase Nominal Voltage L-N (V-sec) | General | Nominal Voltage |  |  | TRUE |  | FALSE
E50BF | Y | Enable Breaker Failure | Breaker Failure | Breaker Failure |  |  | FALSE |  | FALSE
50BFP | 1.89 | Breaker Failure Pickup | Breaker Failure | Breaker Failure | A |  | FALSE |  | FALSE
BFPU | 9 | Breaker Failure Time Delay (cyc) | Breaker Failure | Breaker Failure | A |  | TRUE |  | FALSE
RTPU | 4 | Retrip Time Delay (cyc) | Breaker Failure | Breaker Failure | A |  | TRUE |  | FALSE
BFI | (TRIP+IN201)*!LT3 | Three-Pole Breaker Failure Initiate | Breaker Failure | Breaker Failure |  |  | FALSE |  | FALSE
BFTR | BFT | Breaker Failure Trip | Breaker Failure | Breaker Failure |  |  | FALSE |  | FALSE
BFULTR | PB4*LT4 | Breaker Failure Unlatch Trip | Breaker Failure | Breaker Failure |  |  | FALSE |  | FALSE
EHBL2 | N | Enable Second Harmonic Blocking | 2nd Harmonic Blocking | Enable |  |  | FALSE |  | FALSE
50LP | 0.25 | Load Detection Phase PU (A-sec) | Trip Logic | Current Detector |  |  | TRUE |  | FALSE
TR | 51P1T+51G1T+!LT2*(SV6T+SV7T)+SV8T+SV9T+81D1T+81D2T | Trip Equation | Trip Logic | Trip |  |  | FALSE |  | TRUE
ULTR | !50L | Unlatch Trip | Trip Logic | Trip |  |  | FALSE |  | FALSE
52A | IN101 | Breaker Status | Close Logic | Status |  |  | FALSE |  | FALSE
CL | SV12T | Close Conditions | Close Logic | Close |  |  | FALSE |  | TRUE
ULCL | TRIP | Unlatch Close | Close Logic | Close |  |  | FALSE |  | FALSE
E79 | N | Enable Reclosures | Close Logic | Reclose |  |  | FALSE |  | FALSE
79RI | 0 | Reclose Initiate | Close Logic | Reclose |  |  | FALSE |  | FALSE
79RIS | 0 | Reclose Initiate Supervision | Close Logic | Reclose |  |  | FALSE |  | FALSE
79DTL | 0 | Drive-to-Lockout | Close Logic | Reclose |  |  | FALSE |  | FALSE
79DLS | 0 | Drive-to-Last Shot | Close Logic | Reclose |  |  | FALSE |  | FALSE
79SKP | 0 | Skip Shot | Close Logic | Reclose |  |  | FALSE |  | FALSE
79STL | 0 | Stall Open Interval Timing | Close Logic | Reclose |  |  | FALSE |  | FALSE
79BRS | 0 | Block Reset Timing | Close Logic | Reclose |  |  | FALSE |  | FALSE
79SEQ | 0 | Sequence Coordination | Close Logic | Reclose |  |  | FALSE |  | FALSE
79CLS | 0 | Reclose Supervision | Close Logic | Reclose |  |  | FALSE |  | FALSE
ESV | 14 | SELogic Variable Timers Enable | SELogic Variables | Enable |  |  | FALSE |  | FALSE
SV1 | IN208 | Trip Coil 1 Alarm | SELogic Variables | Alarm |  |  | FALSE |  | TRUE
SV1PU | 30 | Trip Coil 1 Alarm | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV1DO | 0 | Trip Coil 1 Alarm | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV2 | IN209 | Trip Coil 2 Alarm | SELogic Variables | Alarm |  |  | FALSE |  | TRUE
SV2PU | 30 | Trip Coil 2 Alarm | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV2DO | 0 | Trip Coil 2 Alarm | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV3 | 0 | Not Used | SELogic Variables | Inactive |  |  | FALSE |  | FALSE
SV3PU | 0 | Not Used | SELogic Variables | Inactive |  |  | TRUE |  | FALSE
SV3DO | 0 | Not Used | SELogic Variables | Inactive |  |  | TRUE |  | FALSE
SV4 | LT4*!(PB1+PB2+PB3+PB5+PB6+PB7+PB8+PB9+PB10) | Pushbutton Lock | SELogic Variables | Supervisory |  |  | FALSE |  | FALSE
SV4PU | 18000 | Pushbutton Lock | SELogic Variables | Supervisory |  |  | TRUE |  | FALSE
SV4DO | 0 | Pushbutton Lock | SELogic Variables | Supervisory |  |  | TRUE |  | FALSE
SV5 | !(SV1T+SV2T+!LT2*SV6T+IN204+IN205+IN210+IN211+IN212+!IN214+!IN215+!IN216) | Close Permissive. Block on TCM, dead bus, and breaker alarms | SELogic Variables | Supervisory |  |  | FALSE |  | FALSE
SV5PU | 0 | Close Permissive. Block on TCM, dead bus, and breaker alarms | SELogic Variables | Supervisory |  |  | TRUE |  | FALSE
SV5DO | 0 | Close Permissive. Block on TCM, dead bus, and breaker alarms | SELogic Variables | Supervisory |  |  | TRUE |  | FALSE
SV6 | 27A1+27B1+27C1 | Level 1 Undervoltage Trip | SELogic Variables | V/Freq Protection |  |  | FALSE |  | TRUE
SV6PU | 720 | Level 1 Undervoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV6DO | 0 | Level 1 Undervoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV7 | 0 | Level 2 Undervoltage Trip | SELogic Variables | V/Freq Protection |  |  | FALSE |  | FALSE
SV7 | 27A2+27B2+27C2 | Level 2 Undervoltage Trip | SELogic Variables | V/Freq Protection |  | 2 | FALSE |  | TRUE
SV7PU | 0 | Level 2 Undervoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV7DO | 0 | Level 2 Undervoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV8 | 59A1+59B1+59C1 | Level 1 Overvoltage Trip | SELogic Variables | V/Freq Protection |  |  | FALSE |  | TRUE
SV8PU | 60 | Level 1 Overvoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV8DO | 0 | Level 1 Overvoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV9 | 59A2+59B2+59C2 | Level 2 Overvoltage Trip | SELogic Variables | V/Freq Protection |  |  | FALSE |  | TRUE
SV9PU | 180 | Level 2 Overvoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV9DO | 0 | Level 2 Overvoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV10 | !IN105*IN106 | 86BFH1 Trip Coil Alarm | SELogic Variables | Alarm |  | 1 | FALSE |  | TRUE
SV10 | 0 | Not Used | SELogic Variables | Inactive |  | 2 | FALSE |  | FALSE
SV10PU | 30 | 86BFH1 Trip Coil Alarm | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV10DO | 0 | 86BFH1 Trip Coil Alarm | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV11 | OC*LT1 | 52T1 SCADA Open | SELogic Variables | Control |  |  | FALSE |  | TRUE
SV11PU | 0 | 52T1 SCADA Open | SELogic Variables | Control |  |  | TRUE |  | FALSE
SV11DO | 30 | 52T1 SCADA Open | SELogic Variables | Control |  |  | TRUE |  | FALSE
SV12 | CC*LT1 | 52T1 SCADA Close | SELogic Variables | Control |  |  | FALSE |  | TRUE
SV12PU | 0 | 52T1 SCADA Close | SELogic Variables | Control |  |  | TRUE |  | FALSE
SV12DO | 30 | 52T1 SCADA Close | SELogic Variables | Control |  |  | TRUE |  | FALSE
SV13 | RB2*LT1*!IN203 | 89L1 SCADA Open | SELogic Variables | Control |  |  | FALSE |  | TRUE
SV13PU | 0 | 89L1 SCADA Open | SELogic Variables | Control |  |  | TRUE |  | FALSE
SV13DO | 30 | 89L1 SCADA Open | SELogic Variables | Control |  |  | TRUE |  | FALSE
SV14 | RB3*LT1*!IN203 | 89L1 SCADA Close | SELogic Variables | Control |  |  | FALSE |  | TRUE
SV14PU | 0 | 89L1 SCADA Close | SELogic Variables | Control |  |  | TRUE |  | FALSE
SV14DO | 30 | 89L1 SCADA Close | SELogic Variables | Control |  |  | TRUE |  | FALSE
SET1 | !LT1*PB1*LT4 | Remote Enable | Latch Bits | Supervisory |  |  | FALSE |  | TRUE
RST1 | LT1*PB1*LT4 | Remote Enable | Latch Bits | Supervisory |  |  | FALSE |  | FALSE
SET2 | !LT2*PB2*LT4 | Undervoltage Trip Disable | Latch Bits | Supervisory |  |  | FALSE |  | TRUE
RST2 | LT2*PB2*LT4 | Undervoltage Trip Disable | Latch Bits | Supervisory |  |  | FALSE |  | FALSE
SET3 | !LT3*PB3*LT4 | Breaker Failure Disable | Latch Bits | Supervisory |  |  | FALSE |  | TRUE
RST3 | LT3*PB3*LT4 | Breaker Failure Disable | Latch Bits | Supervisory |  |  | FALSE |  | FALSE
SET4 | !LT4*PB5 | Pushbutton Lock | Latch Bits | Supervisory |  |  | FALSE |  | FALSE
RST4 | LT4*(PB5+/SV4T) | Pushbutton Lock | Latch Bits | Supervisory |  |  | FALSE |  | FALSE
SET5 | 0 | Not Used | Latch Bits | Inactive |  |  | FALSE |  | TRUE
RST5 | 0 | Not Used | Latch Bits | Inactive |  |  | FALSE |  | FALSE
SET6 | SV1T | Trip Coil 1 Alarm | Latch Bits | Alarm |  |  | FALSE |  | TRUE
RST6 | LT4*PB6 | Trip Coil 1 Alarm | Latch Bits | Alarm |  |  | FALSE |  | FALSE
SET7 | SV2T | Trip Coil 2 Alarm | Latch Bits | Alarm |  |  | FALSE |  | TRUE
RST7 | LT4*PB6 | Trip Coil 2 Alarm | Latch Bits | Alarm |  |  | FALSE |  | FALSE
SET8 | 0 | Not Used | Latch Bits | Inactive |  |  | FALSE |  | FALSE
RST8 | 0 | Not Used | Latch Bits | Inactive |  |  | FALSE |  | FALSE
SET9 | SV6T+SV7T+SV8T+SV9T | Voltage Trip Indication | Latch Bits | Alarm |  |  | FALSE |  | TRUE
RST9 | RB1+TRGTR | Voltage Trip Indication | Latch Bits | Alarm |  |  | FALSE |  | FALSE
SET10 | 81D1T+81D2T | Frequency Trip Indication | Latch Bits | Alarm |  |  | FALSE |  | TRUE
RST10 | RB1+TRGTR | Frequency Trip Indication | Latch Bits | Alarm |  |  | FALSE |  | FALSE
SET11 | SV10T | 86BFH1 Trip Coil Alarm | Latch Bits | Alarm |  | 1 | FALSE |  | TRUE
RST11 | LT4*PB6 | 86BFH1 Trip Coil Alarm | Latch Bits | Alarm |  | 1 | FALSE |  | FALSE
SET11 | 0 | Not Used | Latch Bits | Inactive |  | 2 | FALSE |  | FALSE
RST11 | 0 | Not Used | Latch Bits | Inactive |  | 2 | FALSE |  | FALSE
OUT101 | TRIP | 52T1 Protection Trip | Output Contacts | Trip |  |  | FALSE |  | TRUE
OUT102 | SV11T | 52T1 SCADA Open | Output Contacts | Trip |  |  | FALSE |  | TRUE
OUT103 | SV12T | 52T1 SCADA Close | Output Contacts | Close |  |  | FALSE |  | TRUE
OUT104 | BFTRIP | 86BFH1 Breaker Failure Trip | Output Contacts | Breaker Failure |  |  | FALSE |  | TRUE
OUT105 | TRIP+BFTRIP | 11T1 Fault Indicator | Output Contacts | Alarm |  |  | FALSE |  | FALSE
OUT106 | RT | 52T1 Backup Trip | Output Contacts | Trip |  |  | FALSE |  | TRUE
OUT107 | SV5T | Permit Close | Output Contacts | Close |  |  | FALSE |  | TRUE
OUT201 | BFTRIP | 87LP Breaker Failure Transfer Trip | Output Contacts | Breaker Failure |  |  | FALSE |  | FALSE
OUT202 | BFTRIP | 87LS Breaker Failure Transfer Trip | Output Contacts | Breaker Failure |  |  | FALSE |  | FALSE
OUT203 | SV13T | 89L1 Open | Output Contacts | Control |  |  | FALSE |  | FALSE
OUT204 | SV14T | 89L1 Close | Output Contacts | Control |  |  | FALSE |  | FALSE
ALRMOUT | !(SALARM+HALARM) | Relay Alarm. Normally closed, held open | Output Contacts | Alarm |  |  | FALSE |  | FALSE
DP1 | IN105 | 86BFH1 Lockout Status | Display Points | Alarm |  |  | FALSE |  | FALSE
DP1_1 | 86BF LOCKOUT | 86BFH1 Lockout Status | Display Points | Alarm |  |  | FALSE |  | FALSE
DP1_0 | NA | 86BFH1 Lockout Status | Display Points | Alarm |  |  | FALSE |  | FALSE
DP2 | IN202 | 89L1 Status | Display Points | Alarm |  |  | FALSE |  | FALSE
DP2_1 | 89L1 CLOSED | 89L1 Status | Display Points | Alarm |  |  | FALSE |  | FALSE
DP2_0 | 89L1 OPEN | 89L1 Status | Display Points | Alarm |  |  | FALSE |  | FALSE
DP3 | IN204 | Breaker Motor 27DC Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP3_1 | 52 MOTOR DC ALM | Breaker Motor 27DC Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP3_0 | NA | Breaker Motor 27DC Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP4 | IN205 | Breaker Motor Power ATS Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP4_1 | 52 MTR ATS ALM | Breaker Motor Power ATS Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP4_0 | NA | Breaker Motor Power ATS Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP5 | 0 | Not Used | Display Points | Inactive |  |  | FALSE |  | FALSE
DP5_1 | NA | Not Used | Display Points | Inactive |  |  | FALSE |  | FALSE
DP5_0 | NA | Not Used | Display Points | Inactive |  |  | FALSE |  | FALSE
DP6 | IN207 | Breaker Spring Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP6_1 | 52 SPRING ALM | Breaker Spring Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP6_0 | NA | Breaker Spring Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP7 | LT9 | Voltage Trip Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP7_1 | VOLT TRIP | Voltage Trip Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP7_0 | NA | Voltage Trip Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP8 | LT10 | Frequency Trip Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP8_1 | FREQ TRIP | Frequency Trip Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP8_0 | NA | Frequency Trip Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP9 | LT6 | Trip Coil 1 Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP9_1 | TCM1 FAIL | Trip Coil 1 Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP9_0 | NA | Trip Coil 1 Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP10 | LT7 | Trip Coil 2 Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP10_1 | TCM2 FAIL | Trip Coil 2 Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP10_0 | NA | Trip Coil 2 Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP11 | LT11 | Lockout Trip Coil Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP11_1 | 86BF TC FAIL | Lockout Trip Coil Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP11_0 | NA | Lockout Trip Coil Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP12 | IN214 | Loss of DC Close Alarm | Display Points | Inactive |  |  | FALSE |  | FALSE
DP12_1 | NA | Loss of DC Close Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP12_0 | 74DC CL ALM | Loss of DC Close Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP13 | IN215 | Loss of DC Trip 1 Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP13_1 | NA | Loss of DC Trip 1 Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP13_0 | 74DC T1 ALM | Loss of DC Trip 1 Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP14 | IN216 | Loss of DC Trip 2 Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP14_1 | NA | Loss of DC Trip 2 Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP14_0 | 74DC T2 ALM | Loss of DC Trip 2 Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP15 | 0 | Not Used | Display Points | Inactive |  |  | FALSE |  | FALSE
DP15_1 | NA | Not Used | Display Points | Inactive |  |  | FALSE |  | FALSE
DP15_0 | NA | Not Used | Display Points | Inactive |  |  | FALSE |  | FALSE
DP16 | 0 | Not Used | Display Points | Inactive |  |  | FALSE |  | FALSE
DP16_1 | NA | Not Used | Display Points | Inactive |  |  | FALSE |  | FALSE
DP16_0 | NA | Not Used | Display Points | Inactive |  |  | FALSE |  | FALSE
SS1 | 1 | Settings Group 1 Enable | Settings Group Enable | Enable |  |  | FALSE |  | TRUE
SS2 | 0 | Settings Group 2 Enable | Settings Group Enable | Enable |  |  | FALSE |  | FALSE
SS3 | 0 | Settings Group 3 Enable | Settings Group Enable | Enable |  |  | FALSE |  | FALSE
SS4 | 0 | Settings Group 4 Enable | Settings Group Enable | Enable |  |  | FALSE |  | FALSE
SS5 | 0 | Settings Group 5 Enable | Settings Group Enable | Enable |  |  | FALSE |  | FALSE
SS6 | 0 | Settings Group 6 Enable | Settings Group Enable | Enable |  |  | FALSE |  | FALSE
LED1 | LT1 | Remote Enable | LED | Indication |  |  | FALSE |  | FALSE
LED2 | LT2 | Undervoltage Disable | LED | Indication |  |  | FALSE |  | FALSE
LED3 | LT3 | Breaker Failure Disable | LED | Indication |  |  | FALSE |  | FALSE
LED4 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED5 | !LT4 | Operator Lock | LED | Indication |  |  | FALSE |  | FALSE
LED6 | LT6+LT7+LT11 | Trip Coil Failed | LED | Indication |  |  | FALSE |  | FALSE
LED7 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED8 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED9 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED10 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED12 | TRIP | Trip | LED | Indication |  |  | FALSE |  | FALSE
LED12L | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED13 | 51P1+51G1 | OC Pickup | LED | Indication |  |  | FALSE |  | FALSE
LED13L | N | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED14 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED14L | N | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED15 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED15L | N | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED16 | 67P1T+67P2T+67P3T+67G1T | Instantaneous OC Trip | LED | Indication |  |  | FALSE |  | FALSE
LED16L | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED17 | 51P1T+51G1T | TOC Trip | LED | Indication |  |  | FALSE |  | FALSE
LED17L | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED18 | 81D1T+81D2T | Frequency Trip | LED | Indication |  |  | FALSE |  | FALSE
LED18L | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED19 | !LT2*(SV6T+SV7T) | Undervoltage Trip | LED | Indication |  |  | FALSE |  | FALSE
LED19L | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED20 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED20L | N | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED21 | SV8T+SV9T | Overvoltage Trip | LED | Indication |  |  | FALSE |  | FALSE
LED21L | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED25 | 51G1T+67G1T | Ground Trip | LED | Indication |  |  | FALSE |  | FALSE
LED25L | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED26 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED26L | N | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
ER | /67P1+/67P2+/67P3+/51P1+/67G1+/51P1+/SV6+/SV7+/SV8+/SV9+/81D1+/81D2+/52A+\52A+/BFTRIP | Event Report Triggers | Recording | Trigger |  |  | FALSE |  | FALSE
RSTTRGT | RB1 | Target Reset Equation | Reset | Control |  |  | FALSE |  | FALSE
E50P | N | PH OC Enable | Protection Setpoint | Enable |  |  | FALSE |  | FALSE
E51P | 1 | PH TOC Enable | Protection Setpoint | Enable |  |  | FALSE |  | FALSE
E50G | N | GND OC Enable | Protection Setpoint | Enable |  |  | FALSE |  | FALSE
E51G | 1 | GND TOC Enable | Protection Setpoint | Enable |  |  | FALSE |  | FALSE
50P1P | OFF | Level 1 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | TRUE
50P1P | 0 | Level 1 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
50P1P | 0 | Level 1 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
50P1P | 0 | Level 1 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
50P1P | 0 | Level 1 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67P1D | 0 | Level 1 PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
67P1D | 0 | Level 1 PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
67P1D | 0 | Level 1 PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
67P1D | 0 | Level 1 PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
67P1D | 0 | Level 1 PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67P1TC | 1 | Level 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
67P1TC | 0 | Level 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
67P1TC | 0 | Level 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
67P1TC | 0 | Level 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
67P1TC | 0 | Level 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51P1P | 3.78 | Level 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | TRUE
51P1P | 0 | Level 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51P1P | 0 | Level 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51P1P | 0 | Level 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51P1P | 0 | Level 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51P1C | U3 | Level 1 PH TOC Curve | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51P1C | 0 | Level 1 PH TOC Curve | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51P1C | 0 | Level 1 PH TOC Curve | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51P1C | 0 | Level 1 PH TOC Curve | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51P1C | 0 | Level 1 PH TOC Curve | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51P1TD | 1 | Level 1 PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
51P1TD | 0 | Level 1 PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51P1TD | 0 | Level 1 PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51P1TD | 0 | Level 1 PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51P1TD | 0 | Level 1 PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51P1MR | 0 | Level 1 PH TOC Min Response (cyc) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
51P1MR | 0 | Level 1 PH TOC Min Response (cyc) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51P1MR | 0 | Level 1 PH TOC Min Response (cyc) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51P1MR | 0 | Level 1 PH TOC Min Response (cyc) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51P1MR | 0 | Level 1 PH TOC Min Response (cyc) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51P1TC | 1 | Level 1 PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51P1TC | 0 | Level 1 PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51P1TC | 0 | Level 1 PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51P1TC | 0 | Level 1 PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51P1TC | 0 | Level 1 PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
50G1P | OFF | Level 1 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | TRUE
50G1P | 0 | Level 1 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
50G1P | 0 | Level 1 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
50G1P | 0 | Level 1 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
50G1P | 0 | Level 1 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67G1D | 0 | Level 1 GND OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
67G1D | 0 | Level 1 GND OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
67G1D | 0 | Level 1 GND OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
67G1D | 0 | Level 1 GND OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
67G1D | 0 | Level 1 GND OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67G1TC | 1 | Level 1 GND OC Torque Control | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
67G1TC | 0 | Level 1 GND OC Torque Control | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
67G1TC | 0 | Level 1 GND OC Torque Control | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
67G1TC | 0 | Level 1 GND OC Torque Control | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
67G1TC | 0 | Level 1 GND OC Torque Control | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51G1P | 1.25 | Level 1 GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | TRUE
51G1P | 0 | Level 1 GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51G1P | 0 | Level 1 GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51G1P | 0 | Level 1 GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51G1P | 0 | Level 1 GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51G1C | U3 | Level 1 GND TOC Curve | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51G1C | 0 | Level 1 GND TOC Curve | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51G1C | 0 | Level 1 GND TOC Curve | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51G1C | 0 | Level 1 GND TOC Curve | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51G1C | 0 | Level 1 GND TOC Curve | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51G1TD | 1 | Level 1 GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
51G1TD | 0 | Level 1 GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51G1TD | 0 | Level 1 GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51G1TD | 0 | Level 1 GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51G1TD | 0 | Level 1 GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51G1TC | 1 | Level 1 GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51G1TC | 0 | Level 1 GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51G1TC | 0 | Level 1 GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51G1TC | 0 | Level 1 GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51G1TC | 0 | Level 1 GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
E81 | 2 | Enable Frequency Elements | Frequency | Enable |  |  | FALSE |  | FALSE
27B81P | 44.488 | Frequency Undervoltage Block (67% VnomLN) | Frequency | V/Freq Protection |  |  | TRUE |  | FALSE
81D1P | 56 | Underfrequency Level 1 (Hz) | Frequency | V/Freq Protection |  |  | TRUE |  | FALSE
81D1D | 3920 | Underfrequency Level 1 Time Delay (cyc) | Frequency | V/Freq Protection |  |  | TRUE |  | FALSE
81D2P | 64 | Overfrequency Level 1 (Hz) | Frequency | V/Freq Protection |  |  | TRUE |  | FALSE
81D2D | 4480 | Overfrequency Level 1 Time Delay (cyc) | Frequency | V/Freq Protection |  |  | TRUE |  | FALSE
EVOLT | Y | Enable Voltage Elements | Voltage | Enable |  |  | FALSE |  | FALSE
27P1P | 51.128 | Undervoltage Level 1 | Voltage | V/Freq Protection |  |  | TRUE |  | FALSE
27P2P | OFF | Undervoltage Level 2 | Voltage | V/Freq Protection |  |  | TRUE |  | FALSE
59P1P | 86.32 | Overvoltage Level 1 | Voltage | V/Freq Protection |  |  | TRUE |  | FALSE
59P2P | 82.336 | Overvoltage Level 2 | Voltage | V/Freq Protection |  |  | TRUE |  | FALSE
EPORT | Y | Enable Port F | Communications | Port F |  |  | FALSE | PF | FALSE
PROTO | SEL | Protocol | Communications | Port F |  |  | FALSE | PF | FALSE
MAXACC | C | Max Access Level | Communications | Port F |  |  | FALSE | PF | FALSE
SPEED | 19200 | Baud Rate | Communications | Port F |  |  | FALSE | PF | FALSE
BITS | 8 | Data Bits | Communications | Port F |  |  | FALSE | PF | FALSE
PARITY | N | Parity | Communications | Port F |  |  | FALSE | PF | FALSE
STOP | 1 | Stop Bits | Communications | Port F |  |  | FALSE | PF | FALSE
FASTOP | Y | Fast Operate Enable | Communications | Port F |  |  | FALSE | PF | FALSE
EPORT | N | Enable Port 1 | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EPORT | N | Enable Port 2 | Communications | Port 2 |  |  | FALSE | P2 | FALSE
EPORT | N | Enable Port 3 | Communications | Port 3 |  |  | FALSE | P3 | FALSE
EPORT | Y | Enable Port 5 | Communications | Port 5 |  |  | FALSE | P5 | FALSE
SUBNETM | 255.255.255.0 | Subnet Mask | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DEFRTR | 172.31.100.254 | Default Router | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ETELNET | Y | Enable Telnet | Communications | Port 5 |  |  | FALSE | P5 | FALSE
TPORT | 23 | Telnet Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
FASTOP | Y | Fast Operate Enable | Communications | Port 5 |  |  | FALSE | P5 | FALSE
EDNP | 2 | Enable DNP Sessions | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPNUM | 20000 | DNP Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPADR | 1 | DNP Server Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPIP1 | 172.31.100.241 | DNP Client IP Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPTR1 | TCP | DNP Transport Protocol | Communications | Port 5 |  |  | FALSE | P5 | FALSE
REPADR1 | 0 | DNP Client Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPMAP1 | 1 | DNP Session Map | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DVARAI1 | 5 | AI Default Variation | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLA1 | 0 | Current Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLV1 | 0 | Volt Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLM1 | 0 | Misc Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBA1 | 0 | Amps Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBV1 | 0 | Volts Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBM1 | 0 | Misc Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPIP2 | 172.31.100.243 | DNP Client IP Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPTR2 | TCP | DNP Transport Protocol | Communications | Port 5 |  |  | FALSE | P5 | FALSE
REPADR2 | 0 | DNP Client Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPMAP2 | 1 | DNP Session Map | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DVARAI2 | 5 | AI Default Variation | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLA2 | 0 | Current Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLV2 | 0 | Volt Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLM2 | 0 | Misc Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBA2 | 0 | Amps Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBV2 | 0 | Volts Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBM2 | 0 | Misc Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
BI_000 | TIRIG | IRIG Status | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_001 | LED1 | Remote Enable | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_002 | LED2 | Undervoltage Disable | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_003 | LED3 | Breaker Failure Disable | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_004 | LED4 | Breaker Failure | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_005 | LED5 | Operator Lock | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_006 | LED6 | Trip Coil Failed | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_007 | LED7 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_008 | LED8 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_009 | LED9 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_010 | LED10 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_011 | TLED11 | Relay Enabled | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_012 | TLED12 | Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_013 | TLED13 | Overcurrent Pickup | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_014 | TLED14 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_015 | TLED15 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_016 | TLED16 | Instantaneous Overcurrent Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_017 | TLED17 | Time Overcurrent Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_018 | TLED18 | Frequency Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_019 | TLED19 | Undervoltage Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_020 | TLED20 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_021 | TLED21 | Overvoltage Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_022 | TLED22 | A Phase Involved | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_023 | TLED23 | B Phase Involved | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_024 | TLED24 | C Phase Involved | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_025 | TLED25 | Ground Involved | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_026 | TLED26 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_027 | IN101 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_028 | IN102 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_029 | IN105 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_030 | IN106 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_031 | IN202 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_032 | IN203 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_033 | IN204 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_034 | IN205 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_035 | IN207 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_036 | IN208 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_037 | IN209 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_038 | IN210 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_039 | IN211 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_040 | IN212 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_041 | IN214 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_042 | IN215 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_043 | IN216 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_044 | OUT107 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_045 | LT6 | Trip Coil Alarm T1 | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_046 | LT7 | Trip Coil Alarm T2 | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_047 | LT11 | Trip Coil Alarm 86 | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_000 | IA | Current A | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_001 | IB | Current B | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_002 | IC | Current C | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_003 | IG | Current G | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_004 | VA | Voltage A | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_005 | VB | Voltage B | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_006 | VC | Voltage C | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_007 | VAB | Voltage AB | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_008 | VBC | Voltage BC | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_009 | VCA | Voltage CA | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_010 | MW3 | Real Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_011 | MVAR3 | Reactive Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_012 | FREQ | Frequency | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_013 | VDC | Battery Voltage | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_000 | RB1 | Target Reset | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_001 | RB2 | 89L Open | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_002 | RB3 | 89L Close | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_003 | OC | Breaker Open | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_004 | CC | Breaker Close | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
SER1 | TRIP,CLOSE,SV1T,SV2T,SV6T,SV7T,SV8T,SV9T,SV10T,SV11T,SV12T,LT1,LT2,LT3,LT5,LT6,LT7,LT9,LT10,LT11 | SER1 Trigger List (24 Elements Max) | Report | SER |  |  | FALSE |  | TRUE
SER2 | IN101,IN105,IN106,IN201,IN202,IN203,IN204,IN205,IN206,IN207,IN208,IN209,IN210,IN211,IN214,IN215,IN216,OUT101,OUT102,OUT103,OUT104,OUT106,OUT107,ALARM | SER2 Trigger List (24 Elements Max) | Report | SER |  |  | FALSE |  | TRUE
SER3 | SG1,50P1,67P1T,50P2,67P2T,51P1,51P1T,50G1,67G1T,51G1,51G1T,OUT201,OUT202,OUT203,OUT204 | SER3 Trigger List (24 Elements Max) | Report | SER |  |  | FALSE |  | TRUE

## XFMR_487E
SEL-487E XFMR Protection Settings & Logic
Relay Specification
Manufacturer | SEL
Model | SEL-487E
Part # | 0487E3X411XXB0X4H644XXX
Function | XFMR Protection
Front View |  |  |  | Rear View
Relay Classification
Relay ID (RID) | Setpoint Class | Logic Class | IP Address/CIDR Prefix (IPADDR)
87T1P | A | 1 | 172.31.100.81/24
I/O Summary |  |  | Remote Bit Summary
I/O | Description |  | Element | Description | Behavior
IN101 | 52T1 Status (a) |  | RB01 | Target Reset | Pulse
IN102 | 52T1 Status (b)
IN103 | Not Used
IN104 | 86T1P Status
IN105 | 86T1P Trip Coil Monitor
IN106 | MPT1 Sump Pump Alarm |  | Pushbutton Summary
IN107 | Not Used |  | Element | Description | Target LED
OUT101 | 52T1 Protection Trip |  | PB1 | 86T1P Trip Coil Alarm | PB1_LED
OUT102 | 86T1P Lockout Trip |  | PB2 | Not Used | PB2_LED
OUT103 | 11T1 Breaker Failure Initiate |  | PB3 | Not Used | PB3_LED
OUT104 | Not Used |  | PB4 | Not Used | PB4_LED
OUT105 | Not Used |  | PB5 | Not Used | PB5_LED
OUT106 | Not Used |  | PB6 | Not Used | PB6_LED
OUT107 | OLTC Disable |  | PB7 | Not Used | PB7_LED
OUT108 | Relay Fail Alarm |  | PB8 | Not Used | PB8_LED
IN201 | Not Used |  | PB9 | Not Used | PB9_LED
IN202 | Not Used |  | PB10 | Not Used | PB10LED
IN203 | Not Used |  | PB11 | Not Used | PB11LED
IN204 | MPT1 ETM-X Oil Alarm |  | PB12 | Not Used | PB12LED
IN205 | MPT1 26Q-1 Oil Temp alarm
IN206 | MPT1 27-4 UV Alarm (B)
IN207 | MPT1 63PR-X PR Alarm
IN208 | MPT1 63GA-1 Service Alarm
IN209 | MPT1 27-AR Rapid Pressure Alarm
IN210 | MPT1 63SDG Gas Alarm
IN211 | MPT1 PR-4X PR LTC Alarm
IN212 | MPT1 27-X AC Alarm
IN213 | Not Used
IN214 | Not Used
IN215 | Not Used
IN216 | MPT1 BH-X Gas ACC Alarm
IN217 | MPT1 SG-1X Relay Alarm
IN218 | MPT1 PR-1X PR Main Alarm
IN219 | MPT1 LG-X Tank Low Level Alarm
IN220 | MPT1 PR-2X PR Main Alarm
IN221 | MPT(X) Sump Pump Alarm
IN222 | Not Used
IN223 | Not Used
IN224 | Not Used
OUT201 | 87T1P Fault Indicator
OUT202 | Spare
OUT203 | Spare
OUT204 | Not Used
OUT205 | Not Used
OUT206 | Not Used
OUT207 | Not Used
OUT208 | Not Used
Target LED Summary
Target LED | Description | Logic | Latch | LED Color (On, Off) | Setpoint Class
T1_LED | A Phase Diff Trip | 87RA OR 87UA | Y | RO | A
T2_LED | B Phase Diff Trip | 87RB OR 87UB | Y | RO | A
T3_LED | C Phase Diff Trip | 87RC OR 87UC | Y | RO | A
T4_LED | Not Used | NA | Y | RO | A
T5_LED | High Side TOC Trip | 51T01 OR 51T03 | Y | RO | A
T6_LED | Low Side TOC Trip | 51T02 OR 51T04 | Y | RO | A
T7_LED | Low Side Overload | 67TP1 | N | RO | A
T8_LED | High Side REF Trip | REFF1 | Y | RO | A
T9_LED | Low Side REF Trip | REFF2 | Y | RO | A
T10_LED | Volts/Hz Trip | 24D1T | Y | RO | A
T11_LED | Loss of Potential | LOPZ | N | RO | A
T12_LED | IRIG OK | TIRIG | N | GO | A
T13_LED | Not Used | NA | Y | AO | A
T14_LED | Not Used | NA | Y | AO | A
T15_LED | Not Used | NA | Y | AO | A
T16_LED | Not Used | NA | Y | AO | A
T17_LED | Not Used | NA | Y | AO | A
T18_LED | Not Used | NA | Y | AO | A
T19_LED | Not used | NA | Y | AO | A
T20_LED | Not used | NA | Y | AO | A
T21_LED | Not used | NA | Y | AO | A
T22_LED | Not used | NA | Y | AO | A
T23_LED | Not used | NA | Y | AO | A
T24_LED | Not used | NA | Y | AO | A
Ratios & Nominal Voltages |  | Setpoint Class
Terminal | Element | A | B | C | D | E
S | CTRS | 400
T | CTRT | 600
IY1 | CTRY1 | 240
IY2 | CTRY2 | 600
| MV Voltage (kV-LL) | 34.5
V | PTRV | 300
V | VNOMV (V-sec) | 115
| HV Voltage (kV-LL) | 138
Z | PTRZ | 1200
Z | VNOMZ (V-sec) | 115
Short Circuit Current Magnitudes
Relay | Setpoint Class | Fault Location | Relay Input Terminal | 3PH (A-pri) | SLG/2PH-G 3I0 (A-pri)
87T1P | A | POI | IS | 1407 | 2523
87T1P | A | POI | IT | 5629 | 15
87T1P | A | HV Substation Bus | IS | 6820 | 3649
87T1P | A | HV Substation Bus | IT | 6275 | 24
87T1P | A | MV Substation Bus | IS | 2961 | 609
87T1P | A | MV Substation Bus | IT | 11846 | 12423
Differential 87T Settings |  | Setpoint Class
|  | A | B | C | D | E
Base XFMR MVA | MVA | 99
Max XFMR MVA | MVA | 165
HV Full Load Amps at Base (S) | A-pri | 414.1861
HV CT Ratio (S) | CTRS | 400
HV TAP (S) | TAPS | 1.0355
MV Full Load Amps at Base (T) | A-pri | 1656.7443
MV CT Ratio (T) | CTRT | 600
MV TAP (T) | TAPT | 2.7612
Max TAP |  | 2.7612
Min TAP |  | 1.0355
TAP Ratio |  | 2.6667
Nominal Secondary Current | A-sec | 5
O87P Multiplier |  | 0.02
Restrained Op. Current Pickup | O87P (pu) | 0.5
Differential Slope 1 | SLP1 (%) | 35
Differential Slope 2 | SLP2 (%) | 90
Unrestrained Op. Current Pickup | U87P (pu) | 4
Differential Philosophy
The differential slopes are calculated using the formula: Slope = tec + rme + (2 * cte + ltce + cte * ltce) / (1 + ltce) Where: tec is the transformer excitation current error, set to 0.03. rme is the relay measurement error, set to 0.05. cte is the current transformer error, which is 0.01 during normal load conditions and 0.20 for high current conditions. ltce is the load tap changer error, set to 0.10. Per SEL recommendation the U87P element is set based on the maximum bus fault in per-unit of the TAP value while accounting for CT saturation which is conservatively assumed to be 50%. This equates to U87P = 0.5 * I3PH-HV/IFLA-HV or 0.5 * I3PH-MV/IFLA-MV, the greater of the two values should be used and then rounded up to the highest integer value.
Restricted Earth Fault Settings |  | Setpoint Class
HV |  | A | B | C | D | E
Full Load Amps | A-pri | 690.3101
Unbalance, 15%
Operate Quantity |  | IY1
Restraint Quantity | REFRF1 | S
Pickup | REF50G1 (pu) | 0.15
MV |  | A | B | C | D | E
Full Load Amps | A-pri | 2761.2404
Unbalance, 15%
Operate Quantity |  | IY2
Restraint Quantity | REFRF2 | T
Pickup | REF50G2 (pu) | 0.15
Restricted Earth Fault Philosophy
The residual current sensitivity threshold may be set as low as 0.05 times nominal current (0.25 A for 5 A nominal CT current). However, the minimum acceptable value must be greater than any natural 3I0 unbalance resulting from load conditions. Assume 15% unbalance. REF elements are only active in the primary 87TnP relays. REF50Gn > Unbalance AND REF50Gn >= 0.05
PH OC Settings |  | Setpoint Class
Level 1 (Terminal S ¦ Overload Detection ¦ Non-Tripping) |  | A | B | C | D | E
HV Full Load Amps | A-pri | 690.3101
Pickup | 50SP1P (A-sec) | 2.15
Delay | 67SP1D (cyc) | 0
Torque Control | 67SP1TC | 1
Level 1 (Terminal S ¦ OLTC Disable ¦ Non-Tripping) |  | A | B | C | D | E
MV Full Load Amps | A-pri | 2761.2404
Pickup | 50TP1P (A-sec) | 5.75
Delay | 67TP1D (cyc) | 0
Torque Control | 67TP1TC | 1
PH OC Philosophy
Phase instantaneous settings comply with PRC-025-2. The phase instantaneous overcurrent element on the HV terminal is not a tripping element and is used as an overload detector. Pickup set to 125% of the MPT ONAN2 HV FLA rounded down to two decimal places. The phase instantaneous overcurrent element on the MV terminal is not a tripping element and is used to disable the OLTC in the event of a fault. Pickup set to 125% of MPT ONAN2 MV FLA rounded down to two decimal places.
PH TOC Settings |  | Setpoint Class
Level 1 (Terminal S) |  | A | B | C | D | E
Aggegate MVA | MVA | 166.6367
HV Voltage | kV-LL | 138
PRC-025-2, Op. 11 Loadability | A-pri | 906.3047
Min 3PH Fault | A-pri | 1407
Operating Quantity | 51O01 | IMAXSF
Pickup | 51P01 (A-sec) | 2.27
Curve | 51C01 | U3
Time Dial | 51TD01 | 2.01
Torque Control | 51TC01 | 1
Level 1 (Terminal T) |  | A | B | C | D | E
Aggegate MVA | MVA | 166.6367
MV Voltage | kV-LL | 138
Max GSU Turns Ratio |  | 4.4058
PRC-025-2, Op. 11 Loadability | A-pri | 3992.9945
Min 3PH Fault | A-pri | 5629
Operating Quantity | 51O02 | IMAXTF
Pickup | 51P02 (A-sec) | 6.66
Curve | 51C02 | U3
Time Dial | 51TD02 | 1
Torque Control | 51TC02 | 1
PH TOC Philosophy
Set HV pickup per PRC-025-2, Option 11. Terminal S Curve and time dial set to coordinate with downstream protection. Must ride through MPT inrush. Set to hold for 1 second for faults on the transformer secondary and at the remote bus. Terminal T Set MV pickup per PRC-025-2, Option 11. Curve set to U3 and time dial set to coordinate with feeder protection.
GND OC Settings |  | Setpoint Class
Level 1 (Terminal S) |  | A | B | C | D | E
POI Fault Max 3I0 | A-pri | 2523
Pickup | 50SG1P (A-sec) | 7.88
Delay | 67SG1D (cyc) | 6
Torque Control | 67SG1TC | 1
GND OC Philosophy
Terminal S Set HV pickup to 125% of the maximum 3I0 current measured at the relay for a POI fault. Delay is set to 6 cycles.
GND TOC Settings |  | Setpoint Class
Level 1 (Terminal S) |  | A | B | C | D | E
Operating Quantity | 51O03 | 3I0SM
Pickup | 51P03 (A-sec) | 0.7491
Curve | 51C03 | U3
Time Dial | 51TD03 | 6.47
Torque Control | 51TC03 | 1
Level 1 (Terminal T) |  | A | B | C | D | E
Operating Quantity | 51O04 | 3I0TM
Pickup | 51P04 (A-sec) | 2.1978
Curve | 51C04 | U3
Time Dial | 51TD04 | 1
Torque Control | 51TC04 | 1
GND TOC Philosophy
Terminal S Set HV pickup to 33% of HV phase time overcurrent pickup. Set curve to U3 and time dial to hold for 1 second for a fault at the POI. Terminal T Set MV pickup to 33% of MV phase time overcurrent pickup. Set curve to U3 and time dial set to coordinate with feeder protection and to hold for 0.5 seconds for a 34.5kV bus fault. This element does not see faults on the high voltage bus, i.e., the fault magnitude is too low.
Volts per Hertz |  | Setpoint Class
Level 1 |  | A | B | C | D | E
Voltage Source | 24VSRC | Z
Pickup | 24D1P (%) | 110
Delay | 24D1D (sec) | 10
Torque Control | 24TC | 1
Volts per Hertz Philosophy
Overexcitation in a transformer occurs when its magnetic core saturates due to overvoltage or underfrequency. The SEL-487E manages this by calculating the ratio of voltage to frequency (V/Hz) which indicates core flux and excitation levels. The volts per hertz element is set with a pickup ratio of 110% with a delay of 10 seconds.
Settings Table
Setting | Value | Description | Category | Function | Setpoint Class | Logic Class | Float | QuickSet Group | SER
SID | GRVR HL WND | Station Identifier | Global | ID |  |  | FALSE |  | FALSE
CONAM | AEP | Company Name | Global | ID |  |  | FALSE |  | FALSE
PTCONN | WYE | Phase PT Connection | Global | General |  |  | FALSE |  | FALSE
NFREQ | 60 | Nominal Frequency (Hz) | Global | General |  |  | FALSE |  | FALSE
PHROT | ABC | Phase Rotation | Global | General |  |  | FALSE |  | FALSE
FRQST | Z | Primary Frequency Source Terminal | Global | General |  |  | FALSE |  | FALSE
RSTTRGT | RB01 | Target Reset Equation | Global | Control |  |  | FALSE |  | FALSE
EPMU | Y | Enable PMU | Global | PMU |  |  | FALSE |  | FALSE
MFRMT | C37.118 | Message Format | Global | PMU |  |  | FALSE |  | FALSE
MRATE | 60 | Messages per Second | Global | PMU |  |  | FALSE |  | FALSE
PMAPP | N | Type of PMU Application | Global | PMU |  |  | FALSE |  | FALSE
PMLEGCY | Y | Enable Legacy Settings | Global | PMU |  |  | FALSE |  | FALSE
PMID | 1 | PMU Hardware ID | Global | PMU |  |  | FALSE |  | FALSE
PHVOLT | V,Z | Include Voltage Terminal | Global | PMU |  |  | FALSE |  | FALSE
PHCURR | S,T | Include Current Terminal | Global | PMU |  |  | FALSE |  | FALSE
PHDATAV | ALL | Phasor Data Set Voltages | Global | PMU |  |  | FALSE |  | FALSE
PHDATAI | ALL | Phasor Data Set Currents | Global | PMU |  |  | FALSE |  | FALSE
PHNR | F | PMU Float or Integer | Global | PMU |  |  | FALSE |  | FALSE
PHFMT | P | Phasor Format Polar or Rectangular | Global | PMU |  |  | FALSE |  | FALSE
FNR | F | Freq Format Float or Integer | Global | PMU |  |  | FALSE |  | FALSE
SS1 | 1 | Settings Group 1 Enable | Global | Enable |  |  | FALSE |  | TRUE
UTCOFF | -5 | UTC Offset to Local Time | Global | Time |  |  | TRUE |  | FALSE
ERDIG | A | Store Selected (S) or All (A) Relay Word Bits | Report | Event |  |  | FALSE |  | FALSE
SRATE | 2 | Sample Rate of Event Report (kHz) | Report | Event |  |  | FALSE |  | FALSE
LER | 2 | Length of Event Report (seconds) | Report | Event |  |  | TRUE |  | FALSE
PRE | 0.25 | Length of Prefault (seconds) | Report | Event |  |  | TRUE |  | FALSE
ECTTERM | S,T | Enable the Following Current Terminals | Relay Configuration | Enable |  |  | FALSE |  | FALSE
EPTTERM | V,Z | Enable the Following Voltage Terminals | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E87 | S,T | Terminal in the Differential Element | Relay Configuration | Enable |  |  | FALSE |  | FALSE
EPCAL | S,T | Enable the Following Power Terminals | Relay Configuration | Enable |  |  | FALSE |  | FALSE
EREF | 2 | # of Restricted Earth Fault Elements | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E50 | S,T | Definite Time OC Elements Enabled for Terminals | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E51 | 4 | # of Time OC Elements Enabled | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E24 | Y | Volts per Hertz Elements Enabled | Relay Configuration | Enable |  |  | FALSE |  | FALSE
CTRS | 400 | CT Ratio Terminal S | CT Data | Ratio |  |  | FALSE |  | FALSE
CTCONS | Y | CT Connection Terminal S | CT Data | Ratio |  |  | FALSE |  | FALSE
CTRT | 600 | CT Ratio Terminal T | CT Data | Ratio |  |  | FALSE |  | FALSE
CTCONT | Y | CT Connection Terminal T | CT Data | Ratio |  |  | FALSE |  | FALSE
CTRY1 | 240 | CT Ratio Terminal Y1 | CT Data | Ratio |  |  | FALSE |  | FALSE
CTRY2 | 600 | CT Ratio Terminal Y2 | CT Data | Ratio |  |  | FALSE |  | FALSE
CTCONY | 1PH | CT Connection Terminal Y | CT Data | Ratio |  |  | FALSE |  | FALSE
PTRV | 300 | PT Ratio Terminal V | PT Data | Ratio |  |  | TRUE |  | FALSE
PTCONV | Y | PT Connection Terminal V | PT Data | Ratio |  |  | FALSE |  | FALSE
VNOMV | 115 | Nominal LL Voltage Terminal V (V-sec) | PT Data | Ratio |  |  | TRUE |  | FALSE
PTRZ | 1200 | PT Ratio Terminal Z | PT Data | Ratio |  |  | TRUE |  | FALSE
PTCONZ | Y | PT Connection Terminal Z | PT Data | Ratio |  |  | FALSE |  | FALSE
VNOMZ | 115 | Nominal LL Voltage Terminal Z (V-sec) | PT Data | Ratio |  |  | TRUE |  | FALSE
VREFS | Z | Voltage Reference for Terminal S | Voltage Reference Terminal Selection | Config |  |  | FALSE |  | FALSE
VREFT | V | Voltage Reference for Terminal T | Voltage Reference Terminal Selection | Config |  |  | FALSE |  | FALSE
E87TS | 1 | Include Terminal S in the Differential | Differential Element 87T | Differential |  |  | FALSE |  | FALSE
TSCTC | 11 | Terminal S CT Connection Compensation | Differential Element 87T | Differential |  |  | FALSE |  | FALSE
VTERMS | 138 | Terminal S Nominal Voltage (kV) | Differential Element 87T | Differential |  |  | TRUE |  | FALSE
E87TT | 1 | Include Terminal T in the Differential | Differential Element 87T | Differential |  |  | FALSE |  | FALSE
TTCTC | 11 | Terminal T CT Connection Compensation | Differential Element 87T | Differential |  |  | FALSE |  | FALSE
VTERMT | 34.5 | Terminal T Nominal Voltage | Differential Element 87T | Differential |  |  | TRUE |  | FALSE
MVA | 165 | Max Transformer MVA | Differential Element 87T | Differential | A |  | TRUE |  | FALSE
O87P | 0.5 | Differential Element Operating Current Pickup (pu) | Differential Element 87T | Differential | A |  | TRUE |  | FALSE
SLP1 | 35 | Slope 1 Setting (%) | Differential Element 87T | Differential | A |  | TRUE |  | FALSE
SLP2 | 90 | Slope 2 Setting (%) | Differential Element 87T | Differential | A |  | TRUE |  | FALSE
U87P | 4 | Unrestrained Element Current Pickup (pu) | Differential Element 87T | Differential | A |  | TRUE |  | FALSE
E87HB | E | Enable Harmonic Blocked Differential Element. Performs cross-blocking between phases. | Differential Element 87T | Differential |  |  | FALSE |  | FALSE
E87HR | W | Enable Harmonic Restrained Differential Element | Differential Element 87T | Differential |  |  | FALSE |  | FALSE
E87Q | E | Enable Negative Seq Differential Element | Differential Element 87T | Differential |  |  | FALSE |  | FALSE
87QP | 0.3 | Negative Seq Differential Element Operating Current Pickup (pu) | Differential Element 87T | Differential |  |  | TRUE |  | FALSE
SLPQ1 | 25 | Negative Seq Differential Slope (%) | Differential Element 87T | Differential |  |  | TRUE |  | FALSE
87QD | 10 | Negative Seq Differential Element Delay (cyc) | Differential Element 87T | Differential |  |  | TRUE |  | FALSE
PCT2 | 15 | Second Harmonic Percentage (%) | Differential Element 87T | Differential |  |  | TRUE |  | FALSE
PCT4 | 15 | Fourth Harmonic Percentage (%) | Differential Element 87T | Differential |  |  | TRUE |  | FALSE
PCT5 | 35 | Fifth Harmonic Percentage (%) | Differential Element 87T | Differential |  |  | TRUE |  | FALSE
REFRF1 | S | IY1 REF Restraint Qty | Restricted Earth Fault | REF | A |  | FALSE |  | FALSE
REF50G1 | 0.15 | IY1 REF Pickup (pu) | Restricted Earth Fault | REF | A |  | TRUE |  | FALSE
REFRF2 | T | IY2 REF Restraint Qty | Restricted Earth Fault | REF | A |  | FALSE |  | FALSE
REF50G2 | 0.15 | IY2 REF Pickup (pu) | Restricted Earth Fault | REF | A |  | TRUE |  | FALSE
50SP1P | 2.15 | Terminal S PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
50SP1P | 0 | Terminal S PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
50SP1P | 0 | Terminal S PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
50SP1P | 0 | Terminal S PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
50SP1P | 0 | Terminal S PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67SP1D | 0 | Terminal S PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
67SP1D | 0 | Terminal S PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
67SP1D | 0 | Terminal S PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
67SP1D | 0 | Terminal S PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
67SP1D | 0 | Terminal S PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67SP1TC | 1 | Terminal S 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
67SP1TC | 0 | Terminal S 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
67SP1TC | 0 | Terminal S 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
67SP1TC | 0 | Terminal S 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
67SP1TC | 0 | Terminal S 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
50TP1P | 5.75 | Terminal T PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
50TP1P | 0 | Terminal T PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
50TP1P | 0 | Terminal T PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
50TP1P | 0 | Terminal T PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
50TP1P | 0 | Terminal T PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67TP1D | 0 | Terminal T PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
67TP1D | 0 | Terminal T PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
67TP1D | 0 | Terminal T PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
67TP1D | 0 | Terminal T PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
67TP1D | 0 | Terminal T PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67TP1TC | 1 | Terminal T 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
67TP1TC | 0 | Terminal T 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
67TP1TC | 0 | Terminal T 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
67TP1TC | 0 | Terminal T 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
67TP1TC | 0 | Terminal T 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
50SG1P | 7.88 | Terminal S PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
50SG1P | 0 | Terminal S PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
50SG1P | 0 | Terminal S PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
50SG1P | 0 | Terminal S PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
50SG1P | 0 | Terminal S PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67SG1D | 6 | Terminal S PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
67SG1D | 0 | Terminal S PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
67SG1D | 0 | Terminal S PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
67SG1D | 0 | Terminal S PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
67SG1D | 0 | Terminal S PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67SG1TC | 1 | Terminal S 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
67SG1TC | 0 | Terminal S 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
67SG1TC | 0 | Terminal S 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
67SG1TC | 0 | Terminal S 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
67SG1TC | 0 | Terminal S 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51O01 | IMAXSF | HV PH TOC Operate Qty | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51O01 | 0 | HV PH TOC Operate Qty | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51O01 | 0 | HV PH TOC Operate Qty | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51O01 | 0 | HV PH TOC Operate Qty | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51O01 | 0 | HV PH TOC Operate Qty | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51P01 | 2.27 | HV 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
51P01 | 0 | HV 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51P01 | 0 | HV 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51P01 | 0 | HV 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51P01 | 0 | HV 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51C01 | U3 | HV PH TOC Curve | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51C01 | 0 | HV PH TOC Curve | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51C01 | 0 | HV PH TOC Curve | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51C01 | 0 | HV PH TOC Curve | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51C01 | 0 | HV PH TOC Curve | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51TD01 | 2.01 | HV PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
51TD01 | 0 | HV PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51TD01 | 0 | HV PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51TD01 | 0 | HV PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51TD01 | 0 | HV PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51TC01 | 1 | HV PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51TC01 | 0 | HV PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51TC01 | 0 | HV PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51TC01 | 0 | HV PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51TC01 | 0 | HV PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51O02 | IMAXTF | MV PH TOC Operate Qty | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51O02 | 0 | MV PH TOC Operate Qty | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51O02 | 0 | MV PH TOC Operate Qty | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51O02 | 0 | MV PH TOC Operate Qty | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51O02 | 0 | MV PH TOC Operate Qty | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51P02 | 6.66 | MV PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
51P02 | 0 | MV PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51P02 | 0 | MV PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51P02 | 0 | MV PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51P02 | 0 | MV PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51C02 | U3 | MV PH TOC Curve | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51C02 | 0 | MV PH TOC Curve | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51C02 | 0 | MV PH TOC Curve | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51C02 | 0 | MV PH TOC Curve | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51C02 | 0 | MV PH TOC Curve | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51TD02 | 1 | MV PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
51TD02 | 0 | MV PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51TD02 | 0 | MV PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51TD02 | 0 | MV PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51TD02 | 0 | MV PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51TC02 | 1 | MV PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51TC02 | 0 | MV PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51TC02 | 0 | MV PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51TC02 | 0 | MV PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51TC02 | 0 | MV PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51O03 | 3I0SM | HV GND TOC Operate Qty | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51O03 | 0 | HV GND TOC Operate Qty | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51O03 | 0 | HV GND TOC Operate Qty | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51O03 | 0 | HV GND TOC Operate Qty | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51O03 | 0 | HV GND TOC Operate Qty | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51P03 | 0.7491 | HV GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
51P03 | 0 | HV GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51P03 | 0 | HV GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51P03 | 0 | HV GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51P03 | 0 | HV GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51C03 | U3 | HV GND TOC Curve | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51C03 | 0 | HV GND TOC Curve | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51C03 | 0 | HV GND TOC Curve | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51C03 | 0 | HV GND TOC Curve | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51C03 | 0 | HV GND TOC Curve | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51TD03 | 6.47 | HV GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
51TD03 | 0 | HV GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51TD03 | 0 | HV GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51TD03 | 0 | HV GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51TD03 | 0 | HV GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51TC03 | 1 | HV GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51TC03 | 0 | HV GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51TC03 | 0 | HV GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51TC03 | 0 | HV GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51TC03 | 0 | HV GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51O04 | 3I0TM | MV GND TOC Operate Qty | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51O04 | 0 | MV GND TOC Operate Qty | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51O04 | 0 | MV GND TOC Operate Qty | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51O04 | 0 | MV GND TOC Operate Qty | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51O04 | 0 | MV GND TOC Operate Qty | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51P04 | 2.1978 | MV GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
51P04 | 0 | MV GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51P04 | 0 | MV GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51P04 | 0 | MV GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51P04 | 0 | MV GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51C04 | U3 | MV GND TOC Curve | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51C04 | 0 | MV GND TOC Curve | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51C04 | 0 | MV GND TOC Curve | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51C04 | 0 | MV GND TOC Curve | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51C04 | 0 | MV GND TOC Curve | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51TD04 | 1 | MV GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
51TD04 | 0 | MV GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51TD04 | 0 | MV GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51TD04 | 0 | MV GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51TD04 | 0 | MV GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51TC04 | 1 | MV GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51TC04 | 0 | MV GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51TC04 | 0 | MV GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51TC04 | 0 | MV GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51TC04 | 0 | MV GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
24VSRC | Z | V/Hz Voltage Source Terminal | Protection Setpoint | V/Hz | A |  | FALSE |  | FALSE
24VSRC | 0 | V/Hz Voltage Source Terminal | Protection Setpoint | V/Hz | B |  | FALSE |  | FALSE
24VSRC | 0 | V/Hz Voltage Source Terminal | Protection Setpoint | V/Hz | C |  | FALSE |  | FALSE
24VSRC | 0 | V/Hz Voltage Source Terminal | Protection Setpoint | V/Hz | D |  | FALSE |  | FALSE
24VSRC | 0 | V/Hz Voltage Source Terminal | Protection Setpoint | V/Hz | E |  | FALSE |  | FALSE
24D1P | 110 | V/Hz Pickup (%) | Protection Setpoint | V/Hz | A |  | FALSE |  | FALSE
24D1P | 0 | V/Hz Pickup (%) | Protection Setpoint | V/Hz | B |  | FALSE |  | FALSE
24D1P | 0 | V/Hz Pickup (%) | Protection Setpoint | V/Hz | C |  | FALSE |  | FALSE
24D1P | 0 | V/Hz Pickup (%) | Protection Setpoint | V/Hz | D |  | FALSE |  | FALSE
24D1P | 0 | V/Hz Pickup (%) | Protection Setpoint | V/Hz | E |  | FALSE |  | FALSE
24D1D | 10 | V/Hz Delay (sec) | Protection Setpoint | V/Hz | A |  | TRUE |  | FALSE
24D1D | 0 | V/Hz Delay (sec) | Protection Setpoint | V/Hz | B |  | TRUE |  | FALSE
24D1D | 0 | V/Hz Delay (sec) | Protection Setpoint | V/Hz | C |  | TRUE |  | FALSE
24D1D | 0 | V/Hz Delay (sec) | Protection Setpoint | V/Hz | D |  | TRUE |  | FALSE
24D1D | 0 | V/Hz Delay (sec) | Protection Setpoint | V/Hz | E |  | TRUE |  | FALSE
24TC | 1 | V/Hz Torque Control | Protection Setpoint | V/Hz | A |  | FALSE |  | FALSE
24TC | 0 | V/Hz Torque Control | Protection Setpoint | V/Hz | B |  | FALSE |  | FALSE
24TC | 0 | V/Hz Torque Control | Protection Setpoint | V/Hz | C |  | FALSE |  | FALSE
24TC | 0 | V/Hz Torque Control | Protection Setpoint | V/Hz | D |  | FALSE |  | FALSE
24TC | 0 | V/Hz Torque Control | Protection Setpoint | V/Hz | E |  | FALSE |  | FALSE
TRXFMR | 87T OR REFF1 OR REFF2 OR 24D1T | Transformer Trip Conditions | Trip Logic | Trip |  |  | FALSE |  | TRUE
ULTXFMR | TRGTR | Unlatch Trip | Trip Logic | Trip |  |  | FALSE |  | FALSE
TRS | 67SG1T OR 51T01 OR 51T03 | Terminal S Trip Conditions | Trip Logic | Trip |  |  | FALSE |  | TRUE
ULTRS | TRGTR OR NOT (67SG1 OR 51S01 OR 51S03) | Terminal S Unlatch Trip | Trip Logic | Trip |  |  | FALSE |  | FALSE
TRT | 51T02 OR 51T04 | Terminal T Trip Conditions | Trip Logic | Trip |  |  | FALSE |  | TRUE
ULTRT | TRGTR OR NOT (51S02 OR 51S04) | Terminal T Unlatch Trip | Trip Logic | Trip |  |  | FALSE |  | FALSE
TDURD | 9 | Min Trip Duration | Trip Logic | Trip |  |  | TRUE |  | FALSE
ER | R_TRIG 50SG1 OR R_TRIG 51S01 OR R_TRIG 51S02 OR R_TRIG 51S03 OR R_TRIG 51S04 | Event Report Triggers | Trip Logic | Event |  |  | FALSE |  | FALSE
OUT101 | TRIPS OR TRIPT | Trip 52T TC1 | Output Contacts | Trip |  |  | FALSE |  | TRUE
OUT102 | TRPXFMR | Trip 86T | Output Contacts | Trip |  |  | FALSE |  | TRUE
OUT103 | TRPXFMR OR TRIPS OR TRIPT | BFI | Output Contacts | Breaker Failure |  |  | FALSE |  | TRUE
OUT104 | NA | Not Used | Output Contacts | Inactive |  |  | FALSE |  | TRUE
OUT105 | NA | Not Used | Output Contacts | Inactive |  |  | FALSE |  | TRUE
OUT106 | NA | Not Used | Output Contacts | Inactive |  |  | FALSE |  | TRUE
OUT107 | 67TP1T | OLTC Disable | Output Contacts | Supervisory |  |  | FALSE |  | TRUE
OUT108 | NOT (SALARM OR HALARM) | Relay Alarm | Output Contacts | Alarm |  |  | FALSE |  | TRUE
OUT201 | TRIPS OR TRIPT OR TRPXFMR | 87T Fault Indicator | Output Contacts | Alarm |  |  | FALSE |  | TRUE
OUT202 | NA | Not Used | Output Contacts | Inactive |  |  | FALSE |  | TRUE
OUT203 | NA | Not Used | Output Contacts | Inactive |  |  | FALSE |  | TRUE
OUT204 | NA | Not Used | Output Contacts | Inactive |  |  | FALSE |  | TRUE
OUT205 | NA | Not Used | Output Contacts | Inactive |  |  | FALSE |  | TRUE
OUT206 | NA | Not Used | Output Contacts | Inactive |  |  | FALSE |  | TRUE
OUT207 | NA | Not Used | Output Contacts | Inactive |  |  | FALSE |  | TRUE
OUT208 | NA | Not Used | Output Contacts | Inactive |  |  | FALSE |  | TRUE
PROTSEL1 | # 86 TCM | 86T Trip Coil Monitor | Logic | Alarm |  |  | FALSE |  | FALSE
PROTSEL2 | PCT01PU := 30.0 | 86T Trip Coil Monitor | Logic | Alarm |  |  | FALSE |  | FALSE
PROTSEL3 | PCT01DO := 0.0 | 86T Trip Coil Monitor | Logic | Alarm |  |  | FALSE |  | FALSE
PROTSEL4 | PCT01IN := NOT IN104 AND IN105 | 86T Trip Coil Monitor | Logic | Alarm |  |  | FALSE |  | FALSE
PROTSEL5 | PLT01S := PCT01Q | 86T Trip Coil Monitor | Logic | Alarm |  |  | FALSE |  | TRUE
PROTSEL6 | PLT01R := PLT01 AND PB1_PUL | 86T Trip Coil Monitor | Logic | Alarm |  |  | FALSE |  | FALSE
PROTSEL7 | # | [5 empty] | FALSE |  | FALSE
PROTSEL8 | # | [5 empty] | FALSE |  | FALSE
PROTSEL9 | # | [5 empty] | FALSE |  | FALSE
PROTSEL10 | # | [5 empty] | FALSE |  | FALSE
PROTSEL11 | # | [5 empty] | FALSE |  | FALSE
PROTSEL12 | # | [5 empty] | FALSE |  | FALSE
PROTSEL13 | # | [5 empty] | FALSE |  | FALSE
PROTSEL14 | # | [5 empty] | FALSE |  | FALSE
PROTSEL15 | # | [5 empty] | FALSE |  | FALSE
PROTSEL16 | # | [5 empty] | FALSE |  | FALSE
PROTSEL17 | # | [5 empty] | FALSE |  | FALSE
PROTSEL18 | # | [5 empty] | FALSE |  | FALSE
PROTSEL19 | # | [5 empty] | FALSE |  | FALSE
PROTSEL20 | # | [5 empty] | FALSE |  | FALSE
PROTSEL21 | # | [5 empty] | FALSE |  | FALSE
PROTSEL22 | # | [5 empty] | FALSE |  | FALSE
PROTSEL23 | # | [5 empty] | FALSE |  | FALSE
PROTSEL24 | # | [5 empty] | FALSE |  | FALSE
PROTSEL25 | # | [5 empty] | FALSE |  | FALSE
AUTO_1 | # | [5 empty] | FALSE |  | FALSE
AUTO_2 | # | [5 empty] | FALSE |  | FALSE
AUTO_3 | # | [5 empty] | FALSE |  | FALSE
AUTO_4 | # | [5 empty] | FALSE |  | FALSE
AUTO_5 | # | [5 empty] | FALSE |  | FALSE
AUTO_6 | # | [5 empty] | FALSE |  | FALSE
AUTO_7 | # | [5 empty] | FALSE |  | FALSE
AUTO_8 | # | [5 empty] | FALSE |  | FALSE
AUTO_9 | # | [5 empty] | FALSE |  | FALSE
AUTO_10 | # | [5 empty] | FALSE |  | FALSE
AUTO_11 | # | [5 empty] | FALSE |  | FALSE
AUTO_12 | # | [5 empty] | FALSE |  | FALSE
AUTO_13 | # | [5 empty] | FALSE |  | FALSE
AUTO_14 | # | [5 empty] | FALSE |  | FALSE
AUTO_15 | # | [5 empty] | FALSE |  | FALSE
AUTO_16 | # | [5 empty] | FALSE |  | FALSE
AUTO_17 | # | [5 empty] | FALSE |  | FALSE
AUTO_18 | # | [5 empty] | FALSE |  | FALSE
AUTO_19 | # | [5 empty] | FALSE |  | FALSE
AUTO_20 | # | [5 empty] | FALSE |  | FALSE
AUTO_21 | # | [5 empty] | FALSE |  | FALSE
AUTO_22 | # | [5 empty] | FALSE |  | FALSE
AUTO_23 | # | [5 empty] | FALSE |  | FALSE
AUTO_24 | # | [5 empty] | FALSE |  | FALSE
AUTO_25 | # | [5 empty] | FALSE |  | FALSE
DP_ELE1 | PLT01 | 86T TC Fail | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET1 | 86T TC FAIL | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR1 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE2 | IN106 | Main MPT Sump Pump Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET2 | MPT1 SUMP ALM | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR2 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE3 | IN204 | MPT ETM Alarms | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET3 | MPT ETM ALMS | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR3 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE4 | IN205 | MPT 26Q-1 Main Tank Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET4 | MPT 26Q1 MAIN ALM | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR4 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE5 | IN206 | MPT Fan Ctrl AC Undervoltage | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET5 | MPT 27-4 FAN ALM | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR5 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE6 | IN207 | MPT Gas Pressure Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET6 | MPT 63PR-1/2 ALM | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR6 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE7 | IN208 | 63GA-1 Relay Service Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET7 | MPT 63GA-1 ALM | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR7 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE8 | IN209 | MPT 27-AR Pressure Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET8 | MPT 27-AR PRES ALM | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR8 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE9 | IN210 | MPT Hydran Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET9 | MPT 63SDG GAS ALM | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR9 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE10 | IN211 | MPT LTC Tank Pressure Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET10 | MPT LTC PR-4X ALM | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR10 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE11 | IN212 | MPT AC Undervoltage | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET11 | MPT 27-1/2/3 AC ALM | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR11 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE12 | IN216 | MPT Gas Acc Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET12 | MPT BH-1X GAS ALM | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR12 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE13 | IN217 | MPT SG-1X Relay Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET13 | MPT SG-1X ALM | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR13 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE14 | IN218 | MPT Main Tank Pressure Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET14 | MPT MAIN PR-1X ALM | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR14 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE15 | IN219 | MPT Low Oil Level Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET15 | MPT LG LOW OIL ALM | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR15 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE16 | IN220 | MPT Main Tank Pressure Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET16 | MPT MAIN PR-2X ALM | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR16 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_ELE17 | IN221 | Backup MPT Sump Pump Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET17 | MPT(X) SUMP ALM | Set Message | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_CLR17 |  | Clear Message | Display Points | Alarm |  |  | FALSE |  | FALSE
PB1_LED | PLT01 | 86T Trip Coil Alarm | LED | Alarm |  |  | FALSE |  | FALSE
PB1_COL | RO | LED Color | LED | Alarm |  |  | FALSE |  | FALSE
PB2_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
PB2_COL | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
PB3_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
PB3_COL | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
PB4_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
PB4_COL | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
PB5_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
PB5_COL | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
PB6_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
PB6_COL | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
PB7_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
PB7_COL | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
PB8_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
PB8_COL | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
PB9_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
PB9_COL | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
PB10LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
PB10COL | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
PB11LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
PB11COL | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
PB12LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
PB12COL | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
T1_LED | 87RA OR 87UA | A Ph Diff Trip | LED | Indication |  |  | FALSE |  | FALSE
T1LEDL | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
T1LEDC | RO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
T2_LED | 87RB OR 87UB | B Ph Diff Trip | LED | Indication |  |  | FALSE |  | FALSE
T2LEDL | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
T2LEDC | RO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
T3_LED | 87RC OR 87UC | C Ph Diff Trip | LED | Indication |  |  | FALSE |  | FALSE
T3LEDL | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
T3LEDC | RO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
T4_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
T4LEDL | N | LED Latch | LED | Inactive |  |  | FALSE |  | FALSE
T4LEDC | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
T5_LED | 51T01 OR 51T03 | HV TOC Trip | LED | Indication |  |  | FALSE |  | FALSE
T5LEDL | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
T5LEDC | RO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
T6_LED | 51T02 OR 51T04 | MV TOC Trip | LED | Indication |  |  | FALSE |  | FALSE
T6LEDL | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
T6LEDC | RO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
T7_LED | 67TP1 | Low Side Overload | LED | Indication |  |  | FALSE |  | FALSE
T7LEDL | N | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
T7LEDC | RO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
T8_LED | REFF1 | HV REF Trip | LED | Indication |  |  | FALSE |  | FALSE
T8LEDL | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
T8LEDC | RO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
T9_LED | REFF2 | MV REF Trip | LED | Indication |  |  | FALSE |  | FALSE
T9LEDL | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
T9LEDC | RO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
T10_LED | 24D1T | V/Hz Trip | LED | Indication |  |  | FALSE |  | FALSE
T10LEDL | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
T10LEDC | RO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
T11_LED | LOPZ | Loss of Potential | LED | Indication |  |  | FALSE |  | FALSE
T11LEDL | N | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
T11LEDC | RO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
T12_LED | TIRIG | IRIG OK | LED | Indication |  |  | FALSE |  | FALSE
T12LEDL | N | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
T12LEDC | GO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
T13_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
T13LEDL | N | LED Latch | LED | Inactive |  |  | FALSE |  | FALSE
T13LEDC | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
T14_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
T14LEDL | N | LED Latch | LED | Inactive |  |  | FALSE |  | FALSE
T14LEDC | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
T15_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
T15LEDL | N | LED Latch | LED | Inactive |  |  | FALSE |  | FALSE
T15LEDC | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
T16_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
T16LEDL | N | LED Latch | LED | Inactive |  |  | FALSE |  | FALSE
T16LEDC | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
T17_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
T17LEDL | N | LED Latch | LED | Inactive |  |  | FALSE |  | FALSE
T17LEDC | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
T18_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
T18LEDL | N | LED Latch | LED | Inactive |  |  | FALSE |  | FALSE
T18LEDC | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
T19_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
T19LEDL | N | LED Latch | LED | Inactive |  |  | FALSE |  | FALSE
T19LEDC | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
T20_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
T20LEDL | N | LED Latch | LED | Inactive |  |  | FALSE |  | FALSE
T20LEDC | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
T21_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
T21LEDL | N | LED Latch | LED | Inactive |  |  | FALSE |  | FALSE
T21LEDC | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
T22_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
T22LEDL | N | LED Latch | LED | Inactive |  |  | FALSE |  | FALSE
T22LEDC | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
T23_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
T23LEDL | N | LED Latch | LED | Inactive |  |  | FALSE |  | FALSE
T23LEDC | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
T24_LED | NA | Not Used | LED | Inactive |  |  | FALSE |  | FALSE
T24LEDL | N | LED Latch | LED | Inactive |  |  | FALSE |  | FALSE
T24LEDC | RO | LED Color | LED | Inactive |  |  | FALSE |  | FALSE
SITM1 | IN101 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM2 | IN102 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM3 | IN103 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM4 | IN104 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM5 | IN105 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM6 | IN106 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM7 | IN107 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM8 | IN201 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM9 | IN202 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM10 | IN203 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM11 | IN204 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM12 | IN205 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM13 | IN206 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM14 | IN207 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM15 | IN208 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM16 | IN209 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM17 | IN210 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM18 | IN211 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM19 | IN212 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM20 | IN213 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM21 | IN214 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM22 | IN215 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM23 | IN216 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM24 | IN217 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM25 | IN218 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM26 | IN219 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM27 | IN220 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM28 | IN221 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM29 | IN222 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM30 | IN223 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM31 | IN224 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM32 | OUT101 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM33 | OUT102 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM34 | OUT103 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM35 | OUT104 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM36 | OUT105 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM37 | OUT106 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM38 | OUT107 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM39 | OUT108 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM40 | OUT201 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM41 | OUT202 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM42 | OUT203 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM43 | OUT204 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM44 | OUT205 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM45 | OUT206 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM46 | OUT207 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM47 | OUT208 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM48 | TRPXFMR | SER | Report | SER |  |  | FALSE |  | FALSE
SITM49 | TRIPS | SER | Report | SER |  |  | FALSE |  | FALSE
SITM50 | TRIPT | SER | Report | SER |  |  | FALSE |  | FALSE
SITM51 | 87T | SER | Report | SER |  |  | FALSE |  | FALSE
SITM52 | REFF1 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM53 | REFF2 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM54 | 24D1T | SER | Report | SER |  |  | FALSE |  | FALSE
SITM55 | 51T01 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM56 | 51T02 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM57 | 51T03 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM58 | 51T04 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM59 | PLT01 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM60 | 67SG1T | SER | Report | SER |  |  | FALSE |  | FALSE
ERAQ1 | IASFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ2 | IASFAC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ3 | IBSFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ4 | IBSFAC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ5 | ICSFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ6 | ICSFAC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ7 | IATFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ8 | IATFAC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ9 | IBTFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ10 | IBTFAC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ11 | ICTFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ12 | ICTFAC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ13 | VAVFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ14 | VAVFAC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ15 | VBVFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ16 | VBVFAC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ17 | VCVFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ18 | VCVFAC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ19 | VAZFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ20 | VBZFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
EPORT | Y | Enable Port F | Communications | Port F |  |  | FALSE | PF | FALSE
PROTO | SEL | Protocol | Communications | Port F |  |  | FALSE | PF | FALSE
MAXACC | C | Max Access Level | Communications | Port F |  |  | FALSE | PF | FALSE
SPEED | 19200 | Baud Rate | Communications | Port F |  |  | FALSE | PF | FALSE
DATABIT | 8 | Data Bits | Communications | Port F |  |  | FALSE | PF | FALSE
PARITY | N | Parity | Communications | Port F |  |  | FALSE | PF | FALSE
STOPBIT | 1 | Stop Bits | Communications | Port F |  |  | FALSE | PF | FALSE
FASTOP | Y | Fast Operate Enable | Communications | Port F |  |  | FALSE | PF | FALSE
EPORT | N | Enable Port 1 | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EPORT | N | Enable Port 2 | Communications | Port 2 |  |  | FALSE | P2 | FALSE
EPORT | N | Enable Port 3 | Communications | Port 3 |  |  | FALSE | P3 | FALSE
EPORT | Y | Enable Port 5 | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DEFRTR | 172.31.100.254 | Default Router | Communications | Port 5 |  |  | FALSE | P5 | FALSE
NETMODE | FAILOVER | Operating Mode | Communications | Port 5 |  |  | FALSE | P5 | FALSE
NETPORT | C | Primary Network Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ETELNET | Y | Enable Telnet | Communications | Port 5 |  |  | FALSE | P5 | FALSE
TPORT | 23 | Telnet Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
FASTOP | Y | Fast Operate Enable | Communications | Port 5 |  |  | FALSE | P5 | FALSE
EDNP | 2 | Enable DNP Sessions | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPNUM | 20000 | DNP Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPADR | 1 | DNP Server Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPIP1 | 172.31.100.241 | DNP Client IP Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPTR1 | TCP | DNP Transport Protocol | Communications | Port 5 |  |  | FALSE | P5 | FALSE
REPADR1 | 0 | DNP Client Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPMAP1 | 1 | DNP Session Map | Communications | Port 5 |  |  | FALSE | P5 | FALSE
AIVAR1 | 5 | AI Default Variation | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLA1 | 0 | Current Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLV1 | 0 | Volt Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLM1 | 0 | Misc Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBA1 | 0 | Amps Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBV1 | 0 | Volts Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBM1 | 0 | Misc Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPIP2 | 172.31.100.243 | DNP Client IP Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPTR2 | TCP | DNP Transport Protocol | Communications | Port 5 |  |  | FALSE | P5 | FALSE
REPADR2 | 0 | DNP Client Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPMAP2 | 1 | DNP Session Map | Communications | Port 5 |  |  | FALSE | P5 | FALSE
AIVAR2 | 5 | AI Default Variation | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLA2 | 0 | Current Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLV2 | 0 | Volt Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLM2 | 0 | Misc Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBA2 | 0 | Amps Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBV2 | 0 | Volts Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBM2 | 0 | Misc Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
EPMIP | Y | Enable PMU Comms | Communications | Port 5 |  |  | FALSE | P5 | FALSE
PMOTS1 | TCP | PMU Output1 Transport Scheme | Communications | Port 5 |  |  | FALSE | P5 | FALSE
PMOIPA1 | 172.31.100.38 | PMU Output1 Client IP | Communications | Port 5 |  |  | FALSE | P5 | FALSE
BI_1 | IN101 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_2 | IN102 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_3 | IN104 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_4 | IN105 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_5 | IN106 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_6 | IN204 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_7 | IN205 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_8 | IN206 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_9 | IN207 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_10 | IN208 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_11 | IN209 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_12 | IN210 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_13 | IN211 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_14 | IN212 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_15 | IN216 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_16 | IN217 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_17 | IN218 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_18 | IN219 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_19 | IN220 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_20 | IN221 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_21 | EN_RLY | Relay Enabled | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_22 | TRIPLED | Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_23 | PB1_LED | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_24 | TLED_1 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_25 | TLED_2 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_26 | TLED_3 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_27 | TLED_4 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_28 | TLED_5 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_29 | TLED_6 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_30 | TLED_7 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_31 | TLED_8 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_32 | TLED_9 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_33 | TLED_10 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_34 | TLED_11 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_35 | TLED_12 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_1 | IASFMC | HV Current A | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_2 | IBSFMC | HV Current B | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_3 | ICSFMC | HV Current C | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_4 | IATFMC | MV Current A | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_5 | IBTFMC | MV Current B | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_6 | ICTFMC | MV Current C | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_7 | IY1FMC | Current H0 | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_8 | IY2FMC | Current X0 | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_9 | VAVFMC | MV Voltage A | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_10 | VBVFMC | MV Voltage B | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_11 | VCVFMC | MV Voltage C | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_12 | VAZFMC | HV Voltage A | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_13 | VBZFMC | HV Voltage B | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_14 | VCZFMC | HV Voltage C | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_15 | VABVFMC | MV Voltage AB | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_16 | VBCVFMC | MV Voltage BC | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_17 | VCAVFMC | MV Voltage CA | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_18 | VABZFMC | HV Voltage AB | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_19 | VBCZFMC | HV Voltage BC | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_20 | VCAZFMC | HV Voltage CA | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_21 | 3PSFC | HV 3PH Real Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_22 | 3QSFC | HV 3PH Reactive Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_23 | 3SSFC | HV 3PH Apparent Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_24 | 3PTFC | MV 3PH Real Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_25 | 3QTFC | MV 3PH Reactive Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_26 | 3STFC | MV 3PH Apparent Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_27 | VDC | Battery Voltage | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_1 | RB01 | Target Reset | Communications | DNP 1 |  |  | FALSE | D1 | FALSE

## XFMR_787
SEL-787 XFMR Protection Settings & Logic
Relay Specification
Manufacturer | SEL
Model | SEL-787
Part # | 07872EE1A1A1A79850620
Function | XFMR Protection
Front View |  |  |  | Rear View
Relay Classification
Relay ID (RID) | Setpoint Class | Logic Class | IP Address (IPADDR)
87T1S | A | 1 | 172.31.100.82
I/O Summary |  |  | Remote Bit Summary
I/O | Description |  | Element | Description | Behavior
IN101 | 52T1 Status (a) |  | RB01 | Target Reset | Pulse
IN102 | Not Used
OUT101 | 52T1 Secondary Protection Trip
OUT102 | 86T1S Lockout Trip |  | Pushbutton Summary
OUT103 | Relay Fail Alarm |  | Element | Description | Target LED
IN301 | Spare |  | PB1 | 86T1S Trip Coil Failed (push to reset) | PB1A_LED
IN302 | Spare |  | PB2 | Not Used | PB2A_LED
IN303 | Not Used |  | PB3 | Not Used | PB3A_LED
IN304 | Not Used |  | PB4 | Not Used | PB4A_LED
OUT301 | 11T1 Breaker Failure Initiate |  | PB5 | Not Used | PB5A_LED
OUT302 | Not Used |  | PB6 | Not Used | PB6A_LED
OUT303 | Not Used |  | PB7 | Not Used | PB7A_LED
OUT304 | Not Used |  | PB8 | Not Used | PB8A_LED
IN401 | 86T1S Status
IN402 | 86T1S Trip Coil Monitor
IN403 | Not Used
IN404 | Not Used
OUT401 | Relay Fault Indicator
OUT402 | Not Used
OUT403 | Not Used
OUT404 | Not Used
Ratios & Nominal Voltages |  | Setpoint Class
Terminal | Element | A | B | C | D | E
W1 | CTR1 | 240
W2 | CTR2 | 600
| HV Voltage (kV-LL) | 138
| MV Voltage (kV-LL) | 34.5
| PTR | Not Used
| VNOM (kV-LL) | Not Used
Short Circuit Current Magnitudes
Relay | Setpoint Class | Fault Location | Relay Input Terminal | 3 PH (A-pri) | SLG/2PH-G 3I0 (A-pri)
87T1S | A | POI | IW1 | 1407 | 2523
87T1S | A | POI | IW2 | 5629 | 15
87T1S | A | HV Substation Bus | IW1 | 1569 | 3746
87T1S | A | HV Substation Bus | IW2 | 6275 | 24
87T1S | A | MV Substation Bus | IW1 | 2961 | 609
87T1S | A | MV Substation Bus | IW2 | 11846 | 12423
Differential 87T Settings |  | Setpoint Class
|  | A | B | C | D | E
Max XFMR MVA | MVA | 165
Base XFMR MVA | MVA | 99
HV Full Load Amps at Base (W1) | A-pri | 414.1861
HV CT Ratio (W1) | CTR1 | 240
HV TAP (W1) | TAP1 | 1.7258
MV Full Load Amps at Base (W2) | A-pri | 1656.7443
MV CT Ratio (W2) | CTR2 | 600
MV TAP (W2) | TAP2 | 2.7612
Max TAP |  | 2.7612
Min TAP |  | 1.7258
TAP Ratio |  | 1.6
Nominal Secondary Current | A-sec | 5
O87P Multiplier |  | 0.02
Restrained Op. Current Pickup | O87P (pu) | 0.5
Differential Slope 1 | SLP1 (%) | 35
Differential Slope 2 | SLP2 (%) | 90
Unrestrained Op. Current Pickup | U87P (pu) | 4
Differential Philosophy
Differential current alarm 87AP = 0.25 pu 87AD = 1 sec Differential configuration set to match primary transformer differential protection. See 87T1P for calculations. Restraint current slope 1 limit (per manufacturer’s recommendation) IRS1 = 6.0
PH TOC Settings |  | Setpoint Class
Level 1 (Terminal W1) |  | A | B | C | D | E
Aggegate MVA | MVA | 166.6367
HV Voltage | kV-LL | 138
PRC-025-2, Op. 11 Loadability | A-pri | 906.3047
Min 3PH Fault | A-pri | 1407
Pickup | 51P1P (A-sec) | 3.78
Curve | 51P1C | U3
Time Dial | 51P1TD | 2.01
Torque Control | 51P1TC | 1
Level 1 (Terminal W2) |  | A | B | C | D | E
Aggegate MVA | MVA | 166.6367
HV Voltage | kV-LL | 138
Max GSU Turns Ratio |  | 4.4058
PRC-025-2, Op. 11 Loadability | A-pri | 3992.9945
Min 3PH Fault | A-pri | 5629
Pickup | 51P2P (A-sec) | 6.66
Curve | 51P2C | U3
Time Dial | 51P2TD | 1
Torque Control | 51P2TC | 1
PH TOC Philosophy
Phase time overcurrent settings are in compliance with PRC-025. Winding 1 -> Set equal to Terminal S in 87T1P Winding 2 -> Set equal to Terminal T in 87T1P Min pickup is 0.5.
GND OC Settings |  | Setpoint Class
Level 1 (Terminal W1) |  | A | B | C | D | E
POI Fault Max 3I0 | A-pri | 2523
Pickup | 50G11P (A-sec) | 13.14
Delay | 50G11D (seconds) | 0.1
Torque Control | 50G11TC | 1
GND OC Philosophy
Winding 1 -> Set equal to Terminal S in 87T1P Min pickup is 0.5.
GND TOC Settings |  | Setpoint Class
Level 1 (Terminal W1) |  | A | B | C | D | E
Pickup | 51G1P (A-sec) | 1.25
Curve | 51G1C | U3
Time Dial | 51G1TD | 6.47
Torque Control | 51G1TC | 1
Level 1 (Terminal W2) |  | A | B | C | D | E
Pickup | 51G2P (A-sec) | 2.2
Curve | 51G2C | U3
Time Dial | 51G2TD | 1
Torque Control | 51G2TC | 1
GND TOC Philosophy
Winding 1 -> Set equal to Terminal S in 87T1P Winding 2 -> Set equal to Terminal T in 87T1P Min pickup is 0.5.
Settings Table
Setting | Value | Description | Category | Function | Setpoint Class | Logic Class | Float | QuickSet Group | SER
PHROT | ABC | Phase Rotation | Global | General |  |  | FALSE |  | FALSE
FNOM | 60 | Rated Frequency (Hz) | Global | General |  |  | FALSE |  | FALSE
METHRES | N | Meter Cutoff Threshold | Global | General |  |  | FALSE |  | FALSE
EPMU | N | Enable SynchoPhasor Measurement | Global | General |  |  | FALSE |  | FALSE
RSTTRGT | RB01 | Reset Targets | Global | General |  |  | FALSE |  | FALSE
UTC_OFF | -5 | UTC Offset to Local Time | Global | Time |  |  | TRUE |  | FALSE
TID | GRVR HL WND | Terminal Identifier | Identifier | General |  |  | FALSE |  | FALSE
MVA | 165 | Maximum Transformer Capacity (MVA) | Configuration Settings | General |  |  | TRUE |  | FALSE
ICOM | Y | Define Internal CT Compensation | Configuration Settings | General |  |  | FALSE |  | FALSE
E87W1 | Y | Enable Winding 1 in Differential Element | Configuration Settings | General |  |  | FALSE |  | FALSE
W1CT | WYE | Winding 1 CT Connection | Configuration Settings | General |  |  | FALSE |  | FALSE
CTR1 | 240 | Winding 1 Phase CT Ratio | Configuration Settings | General |  |  | FALSE |  | FALSE
W1CTC | 11 | Winding 1 CT Compensation (filters zero sequence comps) | Configuration Settings | General |  |  | FALSE |  | FALSE
VWDG1 | 138 | Winding 1 Line-to-Line Voltage (kV) | Configuration Settings | General |  |  | FALSE |  | FALSE
E87W2 | Y | Enable Winding 2 in Differential Element | Configuration Settings | General |  |  | FALSE |  | FALSE
W2CT | WYE | Winding 2 CT Connection | Configuration Settings | General |  |  | FALSE |  | FALSE
CTR2 | 600 | Winding 2 Phase CT Ratio | Configuration Settings | General |  |  | FALSE |  | FALSE
W2CTC | 11 | Winding 2 CT Compensation (filters zero sequence comps) | Configuration Settings | General |  |  | FALSE |  | FALSE
VWDG2 | 34.5 | Winding 2 Line-to-Line Voltage (kV) | Configuration Settings | General |  |  | TRUE |  | FALSE
O87P | 0.5 | Restrained Element Operating Current Pickup (pu) | Transformer Differential Elements | Diff |  |  | TRUE |  | FALSE
87AP | 0.25 | Differential Current Alarm Pickup (pu) | Transformer Differential Elements | Diff |  |  | TRUE |  | FALSE
87AD | 1 | Differential Current Alarm Delay (seconds) | Transformer Differential Elements | Diff |  |  | TRUE |  | FALSE
SLP1 | 35 | Restraint Slope 1 Percentage (%) | Transformer Differential Elements | Diff |  |  | FALSE |  | FALSE
SLP2 | 90 | Restraint Slope 2 Percentage (%) | Transformer Differential Elements | Diff |  |  | FALSE |  | FALSE
IRS1 | 6 | Restraint Current Slope 1 Limit (pu) | Transformer Differential Elements | Diff |  |  | TRUE |  | FALSE
U87P | 4 | Unrestrained Element Operating Current Pickup (pu) | Transformer Differential Elements | Diff |  |  | TRUE |  | FALSE
PCT2 | 15 | Second-Harmonic Blocking Percentage (%) | Transformer Differential Elements | Diff |  |  | FALSE |  | FALSE
PCT4 | 15 | Fourth-Harmonic Blocking Percentage (%) | Transformer Differential Elements | Diff |  |  | FALSE |  | FALSE
PCT5 | 35 | Fifth-Harmonic Blocking Percentage (%) | Transformer Differential Elements | Diff |  |  | FALSE |  | FALSE
HRSTR | Y | Enable Harmonic Restraint | Transformer Differential Elements | Diff |  |  | FALSE |  | FALSE
HBLK | Y | Enable Harmonic Blocking | Transformer Differential Elements | Diff |  |  | FALSE |  | FALSE
50G11P | 13.14 | Residual OC Pickup | Winding 1 Residual Overcurrent Elements | Overcurrent | A |  | TRUE |  | FALSE
50G11P | 0 | Residual OC Pickup | Winding 1 Residual Overcurrent Elements | Overcurrent | B |  | TRUE |  | FALSE
50G11P | 0 | Residual OC Pickup | Winding 1 Residual Overcurrent Elements | Overcurrent | C |  | TRUE |  | FALSE
50G11P | 0 | Residual OC Pickup | Winding 1 Residual Overcurrent Elements | Overcurrent | D |  | TRUE |  | FALSE
50G11P | 0 | Residual OC Pickup | Winding 1 Residual Overcurrent Elements | Overcurrent | E |  | TRUE |  | FALSE
50G11D | 0.1 | Time Delay (seconds) | Winding 1 Residual Overcurrent Elements | Overcurrent | A |  | TRUE |  | FALSE
50G11D | 0 | Time Delay | Winding 1 Residual Overcurrent Elements | Overcurrent | B |  | TRUE |  | FALSE
50G11D | 0 | Time Delay | Winding 1 Residual Overcurrent Elements | Overcurrent | C |  | TRUE |  | FALSE
50G11D | 0 | Time Delay | Winding 1 Residual Overcurrent Elements | Overcurrent | D |  | TRUE |  | FALSE
50G11D | 0 | Time Delay | Winding 1 Residual Overcurrent Elements | Overcurrent | E |  | TRUE |  | FALSE
50G11TC | 1 | Torque Control | Winding 1 Residual Time Overcurrent Elements | Overcurrent | A |  | FALSE |  | FALSE
50G11TC | 0 | Torque Control | Winding 1 Residual Time Overcurrent Elements | Overcurrent | B |  | FALSE |  | FALSE
50G11TC | 0 | Torque Control | Winding 1 Residual Time Overcurrent Elements | Overcurrent | C |  | FALSE |  | FALSE
50G11TC | 0 | Torque Control | Winding 1 Residual Time Overcurrent Elements | Overcurrent | D |  | FALSE |  | FALSE
50G11TC | 0 | Torque Control | Winding 1 Residual Time Overcurrent Elements | Overcurrent | E |  | FALSE |  | FALSE
51P1P | 3.78 | Phase TOC Pickup | Winding 1 Phase Time Overcurrent Elements | Overcurrent | A |  | TRUE |  | FALSE
51P1P | 0 | Phase TOC Pickup | Winding 1 Phase Time Overcurrent Elements | Overcurrent | B |  | TRUE |  | FALSE
51P1P | 0 | Phase TOC Pickup | Winding 1 Phase Time Overcurrent Elements | Overcurrent | C |  | TRUE |  | FALSE
51P1P | 0 | Phase TOC Pickup | Winding 1 Phase Time Overcurrent Elements | Overcurrent | D |  | TRUE |  | FALSE
51P1P | 0 | Phase TOC Pickup | Winding 1 Phase Time Overcurrent Elements | Overcurrent | E |  | TRUE |  | FALSE
51P1C | U3 | Curve | Winding 1 Phase Time Overcurrent Elements | Overcurrent | A |  | FALSE |  | FALSE
51P1C | 0 | Curve | Winding 1 Phase Time Overcurrent Elements | Overcurrent | B |  | FALSE |  | FALSE
51P1C | 0 | Curve | Winding 1 Phase Time Overcurrent Elements | Overcurrent | C |  | FALSE |  | FALSE
51P1C | 0 | Curve | Winding 1 Phase Time Overcurrent Elements | Overcurrent | D |  | FALSE |  | FALSE
51P1C | 0 | Curve | Winding 1 Phase Time Overcurrent Elements | Overcurrent | E |  | FALSE |  | FALSE
51P1TD | 2.01 | Time Dial | Winding 1 Phase Time Overcurrent Elements | Overcurrent | A |  | TRUE |  | FALSE
51P1TD | 0 | Time Dial | Winding 1 Phase Time Overcurrent Elements | Overcurrent | B |  | TRUE |  | FALSE
51P1TD | 0 | Time Dial | Winding 1 Phase Time Overcurrent Elements | Overcurrent | C |  | TRUE |  | FALSE
51P1TD | 0 | Time Dial | Winding 1 Phase Time Overcurrent Elements | Overcurrent | D |  | TRUE |  | FALSE
51P1TD | 0 | Time Dial | Winding 1 Phase Time Overcurrent Elements | Overcurrent | E |  | TRUE |  | FALSE
51P1TC | 1 | Torque Control | Winding 1 Phase Time Overcurrent Elements | Overcurrent | A |  | FALSE |  | FALSE
51P1TC | 0 | Torque Control | Winding 1 Phase Time Overcurrent Elements | Overcurrent | B |  | FALSE |  | FALSE
51P1TC | 0 | Torque Control | Winding 1 Phase Time Overcurrent Elements | Overcurrent | C |  | FALSE |  | FALSE
51P1TC | 0 | Torque Control | Winding 1 Phase Time Overcurrent Elements | Overcurrent | D |  | FALSE |  | FALSE
51P1TC | 0 | Torque Control | Winding 1 Phase Time Overcurrent Elements | Overcurrent | E |  | FALSE |  | FALSE
51G1P | 1.25 | Residual TOC Pickup | Winding 1 Residual Time Overcurrent Elements | Overcurrent | A |  | TRUE |  | FALSE
51G1P | 0 | Residual TOC Pickup | Winding 1 Residual Time Overcurrent Elements | Overcurrent | B |  | TRUE |  | FALSE
51G1P | 0 | Residual TOC Pickup | Winding 1 Residual Time Overcurrent Elements | Overcurrent | C |  | TRUE |  | FALSE
51G1P | 0 | Residual TOC Pickup | Winding 1 Residual Time Overcurrent Elements | Overcurrent | D |  | TRUE |  | FALSE
51G1P | 0 | Residual TOC Pickup | Winding 1 Residual Time Overcurrent Elements | Overcurrent | E |  | TRUE |  | FALSE
51G1C | U3 | Curve | Winding 1 Residual Time Overcurrent Elements | Overcurrent | A |  | FALSE |  | FALSE
51G1C | 0 | Curve | Winding 1 Residual Time Overcurrent Elements | Overcurrent | B |  | FALSE |  | FALSE
51G1C | 0 | Curve | Winding 1 Residual Time Overcurrent Elements | Overcurrent | C |  | FALSE |  | FALSE
51G1C | 0 | Curve | Winding 1 Residual Time Overcurrent Elements | Overcurrent | D |  | FALSE |  | FALSE
51G1C | 0 | Curve | Winding 1 Residual Time Overcurrent Elements | Overcurrent | E |  | FALSE |  | FALSE
51G1TD | 6.47 | Time Dial | Winding 1 Residual Time Overcurrent Elements | Overcurrent | A |  | TRUE |  | FALSE
51G1TD | 0 | Time Dial | Winding 1 Residual Time Overcurrent Elements | Overcurrent | B |  | TRUE |  | FALSE
51G1TD | 0 | Time Dial | Winding 1 Residual Time Overcurrent Elements | Overcurrent | C |  | TRUE |  | FALSE
51G1TD | 0 | Time Dial | Winding 1 Residual Time Overcurrent Elements | Overcurrent | D |  | TRUE |  | FALSE
51G1TD | 0 | Time Dial | Winding 1 Residual Time Overcurrent Elements | Overcurrent | E |  | TRUE |  | FALSE
51G1TC | 1 | Torque Control | Winding 1 Residual Time Overcurrent Elements | Overcurrent | A |  | FALSE |  | FALSE
51G1TC | 0 | Torque Control | Winding 1 Residual Time Overcurrent Elements | Overcurrent | B |  | FALSE |  | FALSE
51G1TC | 0 | Torque Control | Winding 1 Residual Time Overcurrent Elements | Overcurrent | C |  | FALSE |  | FALSE
51G1TC | 0 | Torque Control | Winding 1 Residual Time Overcurrent Elements | Overcurrent | D |  | FALSE |  | FALSE
51G1TC | 0 | Torque Control | Winding 1 Residual Time Overcurrent Elements | Overcurrent | E |  | FALSE |  | FALSE
51P2P | 6.66 | Phase TOC Pickup | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | A |  | TRUE |  | FALSE
51P2P | 0 | Phase TOC Pickup | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | B |  | TRUE |  | FALSE
51P2P | 0 | Phase TOC Pickup | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | C |  | TRUE |  | FALSE
51P2P | 0 | Phase TOC Pickup | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | D |  | TRUE |  | FALSE
51P2P | 0 | Phase TOC Pickup | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | E |  | TRUE |  | FALSE
51P2C | U3 | Curve | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | A |  | FALSE |  | FALSE
51P2C | 0 | Curve | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | B |  | FALSE |  | FALSE
51P2C | 0 | Curve | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | C |  | FALSE |  | FALSE
51P2C | 0 | Curve | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | D |  | FALSE |  | FALSE
51P2C | 0 | Curve | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | E |  | FALSE |  | FALSE
51P2TD | 1 | Time Dial | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | A |  | TRUE |  | FALSE
51P2TD | 0 | Time Dial | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | B |  | TRUE |  | FALSE
51P2TD | 0 | Time Dial | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | C |  | TRUE |  | FALSE
51P2TD | 0 | Time Dial | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | D |  | TRUE |  | FALSE
51P2TD | 0 | Time Dial | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | E |  | TRUE |  | FALSE
51P2TC | 1 | Torque Control | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | A |  | FALSE |  | FALSE
51P2TC | 0 | Torque Control | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | B |  | FALSE |  | FALSE
51P2TC | 0 | Torque Control | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | C |  | FALSE |  | FALSE
51P2TC | 0 | Torque Control | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | D |  | FALSE |  | FALSE
51P2TC | 0 | Torque Control | Winding 2 Max Phase Time Overcurrent Element | Overcurrent | E |  | FALSE |  | FALSE
51G2P | 2.2 | Residual TOC Pickup | Winding 2 Residual Time Overcurrent Elements | Overcurrent | A |  | TRUE |  | FALSE
51G2P | 0 | Residual TOC Pickup | Winding 2 Residual Time Overcurrent Elements | Overcurrent | B |  | TRUE |  | FALSE
51G2P | 0 | Residual TOC Pickup | Winding 2 Residual Time Overcurrent Elements | Overcurrent | C |  | TRUE |  | FALSE
51G2P | 0 | Residual TOC Pickup | Winding 2 Residual Time Overcurrent Elements | Overcurrent | D |  | TRUE |  | FALSE
51G2P | 0 | Residual TOC Pickup | Winding 2 Residual Time Overcurrent Elements | Overcurrent | E |  | TRUE |  | FALSE
51G2C | U3 | Curve | Winding 2 Residual Time Overcurrent Elements | Overcurrent | A |  | FALSE |  | FALSE
51G2C | 0 | Curve | Winding 2 Residual Time Overcurrent Elements | Overcurrent | B |  | FALSE |  | FALSE
51G2C | 0 | Curve | Winding 2 Residual Time Overcurrent Elements | Overcurrent | C |  | FALSE |  | FALSE
51G2C | 0 | Curve | Winding 2 Residual Time Overcurrent Elements | Overcurrent | D |  | FALSE |  | FALSE
51G2C | 0 | Curve | Winding 2 Residual Time Overcurrent Elements | Overcurrent | E |  | FALSE |  | FALSE
51G2TD | 1 | Time Dial | Winding 2 Residual Time Overcurrent Elements | Overcurrent | A |  | TRUE |  | FALSE
51G2TD | 0 | Time Dial | Winding 2 Residual Time Overcurrent Elements | Overcurrent | B |  | TRUE |  | FALSE
51G2TD | 0 | Time Dial | Winding 2 Residual Time Overcurrent Elements | Overcurrent | C |  | TRUE |  | FALSE
51G2TD | 0 | Time Dial | Winding 2 Residual Time Overcurrent Elements | Overcurrent | D |  | TRUE |  | FALSE
51G2TD | 0 | Time Dial | Winding 2 Residual Time Overcurrent Elements | Overcurrent | E |  | TRUE |  | FALSE
51G2TC | 1 | Torque Control | Winding 2 Residual Time Overcurrent Elements | Overcurrent | A |  | FALSE |  | FALSE
51G2TC | 0 | Torque Control | Winding 2 Residual Time Overcurrent Elements | Overcurrent | B |  | FALSE |  | FALSE
51G2TC | 0 | Torque Control | Winding 2 Residual Time Overcurrent Elements | Overcurrent | C |  | FALSE |  | FALSE
51G2TC | 0 | Torque Control | Winding 2 Residual Time Overcurrent Elements | Overcurrent | D |  | FALSE |  | FALSE
51G2TC | 0 | Torque Control | Winding 2 Residual Time Overcurrent Elements | Overcurrent | E |  | FALSE |  | FALSE
TDURD | 0.5 | Minimum Trip Time (seconds) | Trip Logic | Trip |  |  | TRUE |  | FALSE
TRXFMR | 87R OR 87U | Trip XFMR Equation | Trip Logic | Trip |  |  | FALSE |  | TRUE
ULTRXFMR | TRGTR OR NOT (87R OR 87U) | Unlatch XFMR Trip | Trip Logic | Trip |  |  | FALSE |  | FALSE
TR1 | 50G11T OR 51P1T OR 51G1T | Trip 1 | Trip Logic | Trip |  |  | FALSE |  | TRUE
ULTRIP1 | TRGTR OR NOT (50G11P OR 51P1P OR 51G1P) | Trip 1 Unlatch | Trip Logic | Trip |  |  | FALSE |  | FALSE
52A1 | IN101 | Breaker Status | Trip Logic | Trip |  |  | FALSE |  | FALSE
TR2 | 51P2T OR 51G2T | Trip 2 | Trip Logic | Trip |  |  | FALSE |  | TRUE
ULTRIP2 | TRGTR OR NOT (51P2P OR 51G2T) | Trip 2 Unlatch | Trip Logic | Trip |  |  | FALSE |  | FALSE
OUT101 | TRIP1 OR TRIP2 | Trip 52T1 | Outputs | Trip |  |  | FALSE |  | FALSE
OUT101FS | N | Fail-Safe Enable | Outputs | Trip |  |  | FALSE |  | FALSE
OUT102 | TRIPXFMR | Trip 86T1S | Outputs | Trip |  |  | FALSE |  | FALSE
OUT102FS | N | Fail-Safe Enable | Outputs | Trip |  |  | FALSE |  | FALSE
OUT103 | NOT (SALARM OR HALARM) | Relay Alarm | Outputs | Alarm |  |  | FALSE |  | FALSE
OUT103FS | N | Fail-Safe Enable | Outputs | Alarm |  |  | FALSE |  | FALSE
OUT301 | TRIP1 OR TRIP2 OR TRIPXFMR | 11T1 Breaker Failure Initiate | Outputs | Trip |  |  | FALSE |  | FALSE
OUT301FS | N | Fail-Safe Enable | Outputs | Trip |  |  | FALSE |  | FALSE
OUT401 | TRIP1 OR TRIP2 OR TRIPXFMR | Relay Fault Indicator | Outputs | Alarm |  |  | FALSE |  | FALSE
OUT401FS | N | Fail-Safe Enable | Outputs | Alarm |  |  | FALSE |  | FALSE
ELAT | 1 | Latch Enable (#) | Latches | Enable |  |  | FALSE |  | FALSE
ESV | 1 | SEL Variable Enable (#) | SEL Variables | Enable |  |  | FALSE |  | FALSE
SV01PU | 0.5 | 86TnS Trip Coil Monitor (seconds) | SEL Variables | Alarm |  |  | TRUE |  | FALSE
SV01DO | 0 | 86TnS Trip Coil Monitor (seconds) | SEL Variables | Alarm |  |  | TRUE |  | FALSE
SV01 | NOT IN401 AND IN402 | 86TnS Trip Coil Monitor | SEL Variables | Alarm |  |  | FALSE |  | FALSE
SET01 | SV01T | 86TnS Trip Coil Monitor | Latches | Alarm |  |  | FALSE |  | FALSE
RST01 | LT01 AND PB01_PUL | 86TnS Trip Coil Monitor | Latches | Alarm |  |  | FALSE |  | FALSE
PB1A_LED | LT01 | 86TnS Trip Coil Monitor | Pushbuttons | Alarm |  |  | FALSE |  | TRUE
PB1ALEDC | RO | 86TnS Trip Coil Monitor | Pushbuttons | Alarm |  |  | FALSE |  | FALSE
T01_LED | 87R OR 87U | Diff Trip | LEDs | Indication |  |  | FALSE |  | FALSE
T01LEDL | Y | Diff Trip | LEDs | Indication |  |  | FALSE |  | FALSE
T01LEDC | R | Diff Trip | LEDs | Indication |  |  | FALSE |  | FALSE
T02_LED | 0 | Not Used | LEDs | Indication |  |  | FALSE |  | FALSE
T02LEDL | Y | Not Used | LEDs | Indication |  |  | FALSE |  | FALSE
T02LEDC | R | Not Used | LEDs | Indication |  |  | FALSE |  | FALSE
T03_LED | 51P1T OR 51G1T | HV TOC Trip | LEDs | Indication |  |  | FALSE |  | FALSE
T03LEDL | Y | HV TOC Trip | LEDs | Indication |  |  | FALSE |  | FALSE
T03LEDC | R | HV TOC Trip | LEDs | Indication |  |  | FALSE |  | FALSE
T04_LED | 51P2T OR 51G2T | MV TOC Trip | LEDs | Indication |  |  | FALSE |  | FALSE
T04LEDL | Y | MV TOC Trip | LEDs | Indication |  |  | FALSE |  | FALSE
T04LEDC | R | MV TOC Trip | LEDs | Indication |  |  | FALSE |  | FALSE
DP05 | 87AT,,"DIFF CUR ALM" | Differential Current Alarm | Display Points | Indication |  |  | FALSE |  | FALSE
SER1 | IN101,IN401,OUT101,OUT102,OUT103,OUT301,PB01,52A1,TRIP1,TRIP2,TRIPXFMR | SER | Report | SER |  |  | FALSE |  | FALSE
SER2 | 51P1T,51G1T,51P2T,51G2T,87U,87R | SER | Report | SER |  |  | FALSE |  | FALSE
SER3 | RB01 | SER | Report | SER |  |  | FALSE |  | FALSE
SER4 | SALARM | SER | Report | SER |  |  | FALSE |  | FALSE
ER | R_TRIG SV01T | Event Report Trigger | Report | Event |  |  | FALSE |  | FALSE
LER | 64 | Length of Event Report (cycles) | Report | Event |  |  | FALSE |  | FALSE
PRE | 20 | Prefault Length (cycles) | Report | Event |  |  | FALSE |  | FALSE
PROTO | SEL | Protocol | Communications | Port F |  |  | FALSE | PF | FALSE
SPEED | 19200 | Data Speed (bps) | Communications | Port F |  |  | FALSE | PF | FALSE
FASTOP | Y | Enable Fast Operate | Communications | Port 1 |  |  | FALSE | P1 | FALSE
SUBNETM | 255.255.255.0 | Subnet Mask | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DEFRTR | 172.31.100.254 | Default Router IP Address | Communications | Port 1 |  |  | FALSE | P1 | FALSE
NETMODE | FAILOVER | Operating Mode | Communications | Port 1 |  |  | FALSE | P1 | FALSE
NETPORT | A | Primary Network Port | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ETELNET | Y | Enable Telnet | Communications | Port 1 |  |  | FALSE | P1 | FALSE
TPORT | 23 | Telnet Port | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EFTPSERV | N | Enable FTP | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EHTTP | N | Enable HTTP Server | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EDNP | 2 | Enable DNP Sessions | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPNUM | 20000 | DNP TCP Port | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPADR | 1 | DNP Address | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPIP1 | 172.31.100.241 | DNP Master IP | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPTR1 | TCP | Transport Protocol | Communications | Port 1 |  |  | FALSE | P1 | FALSE
REPADR1 | 0 | DNP Address to Report to | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPMAP1 | 1 | DNP Map Selection | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DVARAI1 | 5 | Analog Input Default Variation | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DECPLA1 | 0 | Currents Scaling Decimal Places | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DECPLV1 | 0 | Voltages Scaling Decimal Places | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DECPLM1 | 0 | Misc Scaling Decimal Places | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ANADBA1 | 0 | Amps Deadband | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ANADBV1 | 0 | Volts Deadband | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ANADBM1 | 0 | Misc Deadband | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPIP2 | 172.31.100.243 | DNP Master IP | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPTR2 | TCP | Transport Protocol | Communications | Port 1 |  |  | FALSE | P1 | FALSE
REPADR2 | 0 | DNP Address to Report to | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPMAP2 | 1 | DNP Map Selection | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DVARAI2 | 5 | Analog Input Default Variation | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DECPLA2 | 0 | Currents Scaling Decimal Places | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DECPLV2 | 0 | Voltages Scaling Decimal Places | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DECPLM2 | 0 | Misc Scaling Decimal Places | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ANADBA2 | 0 | Amps Deadband | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ANADBV2 | 0 | Volts Deadband | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ANADBM2 | 0 | Misc Deadband | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EPORT | N | Enable Port 2 | Communications | Port 2 |  |  | FALSE | P2 | FALSE
EPORT | Y | Enable Port 3 | Communications | Port 3 |  |  | FALSE | P3 | FALSE
BI_00 | ENABLED | Relay Enabled | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_01 | TRIP_LED | Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_02 | IRIGOK | IRIG Status | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_03 | IN101 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_04 | IN401 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_05 | IN402 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_06 | T01_LED | Differential Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_07 | T02_LED | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_08 | T03_LED | HV TOC Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_09 | T04_LED | MV TOC Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_10 | T05_LED | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_11 | T06_LED | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_12 | PB1A_LED | 86T1S TCM Alarm | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_00 | IAW1_MAG | HV Current A | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_01 | IBW1_MAG | HV Current B | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_02 | ICW1_MAG | HV Current C | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_03 | IAW2_MAG | MV Current A | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_04 | IBW2_MAG | MV Current B | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_05 | ICW2_MAG | MV Current C | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_00 | RB01 | Target Reset | Communications | DNP 1 |  |  | FALSE | D1 | FALSE

## FDR_351S
SEL-351S Feeder Protection Settings & Logic
Relay Specification
Manufacturer | SEL
Model | SEL-351S
Part # | 0351S7XHD3E5441
Function | Feeder Protection
Front View |  |  |  | Rear View
Relay Classification
Relay ID (RID) | Setpoint Class | Logic Class | IP Address (IPADDR)
11F1 | A | 1 | 172.31.100.84
11F2 | B | 2 | 172.31.100.85
11F3 | B | 2 | 172.31.100.86
11F4 | B | 2 | 172.31.100.87
11F5 | B | 2 | 172.31.100.88
11F6 | B | 2 | 172.31.100.89
I/O Summary |  |  | Remote Bit Summary
I/O | Description |  | Element | Description | Behavior
IN101 | 52F Status (a) |  | OC | 52F SCADA Open | Pulse
IN102 | 52F Status (b) |  | CC | 52F SCADA Close | Pulse
IN103 | Not Used |  | RB1 | Target Reset | Pulse
IN104 | Not Used
IN105 | 86BFL1 Status (F1 Only)
IN106 | 86BFL1 Trip Coil Monitor (F1 Only) |  | Pushbutton Summary
OUT101 | 52F Protection Trip (TC1) |  | Element | Description | Target LED
OUT102 | 52F SCADA Trip |  | PB1 | Remote Enable | LED1
OUT103 | 52F SCADA Close |  | PB2 | Undervoltage Disable | LED2
OUT104 | 86BFL1 Lockout Trip |  | PB3 | Breaker Failure Disable | LED3
OUT105 | 11F1 Fault Indicator |  | PB4 | Breaker Failed (push to reset) | LED4
OUT106 | 52F Secondary Trip (TC2) |  | PB5 | Operator Lock (hold for 3 sec) | LED5
OUT107 | 52F Block Close |  | PB6 | Trip Coil Failed (push to reset) | LED6
ALARM | Relay Fail Alarm |  | PB7 | Maintenance Mode Enable | LED7
IN201 | Not Used |  | PB8 | Not Used | LED8
IN202 | 52F Loss of AC Heater |  | PB9 | Not Used | LED9
IN203 | 52F Loss of AC Motor |  | PB10 | Not Used | LED10
IN204 | 52F Spring Alarm
IN205 | 52F Loss of DC Close
IN206 | 52F Loss of DC T1 |  | Ratios & Nominal Voltages
IN207 | 52F Loss of DC T2 |  | Element | Value
IN208 | 52F TCM T1 |  | CT Ratio | 240
IN209 | 52F TCM T2 |  | PT Ratio | 300
IN210 | 52F 43LR Status #1 |  | Collector Voltage (kV LL) | 34.5
IN211 | 52F 43LR Status #2 |  | Relay Nominal Voltage (V-sec LN) | 66.4
IN212 | Spare
IN213 | Not Used
IN214 | 74 DC Close
IN215 | 74 DC T1
IN216 | 74 DC T2
OUT201 | Not Used
OUT202 | Not Used
OUT203 | Not Used
OUT204 | Not Used
Short Circuit Current Magnitudes
Relay | Fault Location |  | 3PH (A-pri) |  | SLG/2PH-G 3I0 (A-pri)
| Closest Fault | Farthest GSU Fault | Closest Fault | Farthest GSU Fault | Closest Fault | Farthest GSU Fault
11F1 | Feeder Side MVCB Terminals | T-40 | 19653 | 11437 | 13551 | 6518
11F2 | Feeder Side MVCB Terminals | T-17 | 19254 | 10820 | 13554 | 6285
11F3 | Feeder Side MVCB Terminals | T-37 | 19254 | 12004 | 13553 | 7103
11F4 | Feeder Side MVCB Terminals | T-38 | 19252 | 12926 | 13547 | 8053
11F5 | Feeder Side MVCB Terminals | T-33 | 19257 | 14069 | 13548 | 9233
11F6 | Feeder Side MVCB Terminals | AT-01 | 19253 | 12617 | 13547 | 7958
PH OC Settings |  | Setpoint Class
Level 1 |  | A | B | C | D | E
Max GSU Inrush | A-pri | 1953 | 2604
Min 3PH Fault | A-pri | 11437 | 10820
Pickup | 50P1P (A-sec) | 8.55 | 11.4
Delay | 67P1D (cyc) | 5 | 5
Torque Control | 67P1TC | 1 | 1
Level 2 (Maintenance Mode) |  | A | B | C | D | E
Max Parasitic Load | KW | 957.069 | 1037.069
Parasitic Load Current | A-pri | 16.0163 | 17.3551
Pickup | 50P2P (A-sec) | 0.25 | 0.25
Delay | 67P2D (cyc) | 0 | 0
Torque Control | 67P2TC | LT8 | LT8
PH OC Philosophy
Phase instantaneous settings comply with PRC-025-2. Level 1 is set to 105% of the total GSU inrush and below the lowest 3 phase fault current magnitude. Level 2 (Maintenance Mode) is set above the feeder’s estimated parasitic load. Since all feeders allow for the pickup to be set above the inrush and below the 3ph fault magnitude at the furthest GSU, no harmonic blocking will be implemented. A 5 cycle delay will be added to allow for coordination with downstream protective equipment. Maintenance Mode can only be used if a feeder is energized and there is no Plant activity on the feeder. Tripping setpoint is very low.
PH TOC Settings |  | Setpoint Class
Level 1 |  | A | B | C | D | E
Max Feeder Aggegate MVA | MVA | 20.331 | 27.108
HV Voltage | kV-LL | 138 | 138
Max GSU Turns Ratio |  | 4.4058 | 4.4058
PRC-025-2, Op. 11 Loadability | A-pri | 487.1771 | 649.5695
Min 3PH Fault | A-pri | 11437 | 10820
Pickup | 51P1P (A-sec) | 2.03 | 2.71
Curve | 51P1C | U3 | U3
Time Dial | 51P1TD | 1 | 1
Minimum Response | 51P1MR (cyc) | 5 | 5
Torque Control | 51P1TC | 1 | 1
PH TOC Philosophy
Set pickup per PRC-025-2, Option 11. Set curve and time dial to coordinate with downstream protection. Set minimum response time to ensure element does not operate before the instantaneous element. Level 1 TOC element must ride through aggregate GSU inrush. PRC-025-2, Option 11 Setting Criteria: The overcurrent element shall be set greater than 130% of the calculated current derived from the maximum aggregate nameplate MVA output at rated power factor (including the Mvar output of any static or dynamic reactive power devices). For facilities where load tap changers are used, the PRC-025-2, Option 11 calculations shall reflect the tap that results in the lowest generator bus voltage.
GND OC Settings |  | Setpoint Class
Level 1 |  | A | B | C | D | E
Max Feeder FLA | A-pri | 340.235 | 453.6467
15% Unbalance | A-pri | 51.0353 | 68.047
80% Min SLG Fault | A-pri | 5214.4 | 5028
Pickup | 50G1P (A-sec) | 1.42 | 1.9
Delay | 67G1D (cyc) | 5 | 5
Torque Control | 67G1TC | 1 | 1
GND OC Philosophy
Set pickup above 15% unbalance and below 80% of lowest GSU ground fault magnitude. Use 100% of generation (FLA) as pickup value. To provide the most economical collector cable neutral sizing, no delay will be used. A value of 10 cycles was used to size the neutrals, instantaneous tripping provides for a total trip time of approximately 4-5 cycles with breaker operating time.
GND TOC Settings |  | Setpoint Class
Level 1 |  | A | B | C | D | E
Min SLG Fault | A-pri | 6518 | 6285
Pickup | 51G1P (A-sec) | 0.61 | 0.81
Curve | 51G1C (cyc) | U3 | U3
Time Dial | 51G1TD | 1 | 1
Torque Control | 51G1TC | 1 | 1
GND TOC Philosophy
Set pickup to 30% of feeder phase time overcurrent pickup. Set curve and time dial to coordinate with downstream protection.
Voltage & Frequency Settings
Description | Pickup |  |  | Logic | Pickup Delay
| Element | Setting Value | Per Unit Value |  | Seconds | Cycles
Freq Undervolt Block | 27B81P (V) | 44.488 | 0.67
Level 1 Underfreq | 81D1P (Hz) | 56.3 | NA |  | 65 | 3659.5
Level 1 Overfreq | 81D2P (Hz) | 63.5 | NA |  | 65 | 4127.5
Level 1 Undervolt | 27P1P (V) | 55.112 | 0.83 | SV6 | 11 | 660
Level 2 Undervolt | 27P2P (V) | OFF | OFF | SV7 | 0 | 0
Level 1 Overvolt | 59P1P (V) | 84.328 | 1.27 | SV8 | 0.7 | 42
Level 2 Overvolt | 59P2P (V) | 81.008 | 1.22 | SV9 | 2.5 | 150
Voltage & Frequency Philosophy
Set to comply with PRC-029-1 and to coordinate with HV and Collector voltage and frequency protection. See PRC-029-1 Appendix for coordination curve.
Settings Table
Setting | Value | Description | Category | Function | Setpoint Class | Logic Class | Float | QuickSet Group | SER
PTCONN | WYE | Phase PT Connection | Global | General |  |  | FALSE |  | FALSE
NFREQ | 60 | Nominal Frequency (Hz) | Global | General |  |  | FALSE |  | FALSE
PHROT | ABC | Phase Rotation | Global | General |  |  | FALSE |  | FALSE
LER | 60 | Length of Event Report (cyc) | Global | General |  |  | FALSE |  | FALSE
PRE | 15 | Cycle Length of Prefault in Event Report (cyc) | Global | General |  |  | FALSE |  | FALSE
UTC_OFF | -5 | UTC Offset to Local Time | Global | Time |  |  | TRUE |  | FALSE
BOOPTCC | PULSE | DNP BO Close/Trip Behavior | Global | DNP |  |  | FALSE |  | FALSE
BOOPPUL | PULSE | DNP BO Pulse On Behavior | Global | DNP |  |  | FALSE |  | FALSE
TID | GRVR HL WND | Terminal Identifier | General | ID |  |  | FALSE |  | FALSE
CTR | 240 | Phase CT Ratio (IA, IB, IC) | General | Ratio |  |  | TRUE |  | FALSE
CTRN | 240 | Neutral CT Ratio (IN) | General | Ratio |  |  | TRUE |  | FALSE
PTR | 300 | Phase PT Ratio (VA, VB, VC) | General | Ratio |  |  | TRUE |  | FALSE
VNOM | 66.4 | Phase Nominal Voltage L-N (V-sec) | General | Nominal Voltage |  |  | TRUE |  | FALSE
E50BF | Y | Enable Breaker Failure | Breaker Failure | Breaker Failure |  |  | FALSE |  | FALSE
50BFP | 1.02 | Breaker Failure Pickup | Breaker Failure | Breaker Failure | A |  | TRUE |  | FALSE
50BFP | 1.36 | Breaker Failure Pickup | Breaker Failure | Breaker Failure | B |  | TRUE |  | FALSE
BFPU | 9 | Breaker Failure Time Delay (cyc) | Breaker Failure | Breaker Failure |  |  | TRUE |  | FALSE
RTPU | 4 | Retrip Time Delay (cyc) | Breaker Failure | Breaker Failure |  |  | TRUE |  | FALSE
BFI | TRIP*!LT3 | Three-Pole Breaker Failure Initiate | Breaker Failure | Breaker Failure |  |  | FALSE |  | FALSE
BFTR | BFT | Breaker Failure Trip | Breaker Failure | Breaker Failure |  |  | FALSE |  | FALSE
BFULTR | PB4*LT4 | Breaker Failure Unlatch Trip | Breaker Failure | Breaker Failure |  |  | FALSE |  | FALSE
50LP | 0.25 | Load Detection Phase PU (A-sec) | Trip Logic | Current Detector |  |  | TRUE |  | FALSE
TR | 67P1T+67P2T+51P1T+67G1T+51G1T+!LT2*(SV6T+SV7T)+SV8T+SV9T+81D1T+81D2T | Trip Equation | Trip Logic | Trip |  |  | FALSE |  | TRUE
ULTR | !50L | Unlatch Trip | Trip Logic | Trip |  |  | FALSE |  | FALSE
52A | IN101 | Breaker Status | Close Logic | Status |  |  | FALSE |  | FALSE
CL | SV12T | Close Conditions | Close Logic | Close |  |  | FALSE |  | TRUE
ULCL | TRIP | Unlatch Close | Close Logic | Close |  |  | FALSE |  | FALSE
E79 | N | Enable Reclosures | Close Logic | Reclose |  |  | FALSE |  | FALSE
79RI | 0 | Reclose Initiate | Close Logic | Reclose |  |  | FALSE |  | FALSE
79RIS | 0 | Reclose Initiate Supervision | Close Logic | Reclose |  |  | FALSE |  | FALSE
79DTL | 0 | Drive-to-Lockout | Close Logic | Reclose |  |  | FALSE |  | FALSE
79DLS | 0 | Drive-to-Last Shot | Close Logic | Reclose |  |  | FALSE |  | FALSE
79SKP | 0 | Skip Shot | Close Logic | Reclose |  |  | FALSE |  | FALSE
79STL | 0 | Stall Open Interval Timing | Close Logic | Reclose |  |  | FALSE |  | FALSE
79BRS | 0 | Block Reset Timing | Close Logic | Reclose |  |  | FALSE |  | FALSE
79SEQ | 0 | Sequence Coordination | Close Logic | Reclose |  |  | FALSE |  | FALSE
79CLS | 0 | Reclose Supervision | Close Logic | Reclose |  |  | FALSE |  | FALSE
ESV | 12 | SELogic Variable Timers Enable | SELogic Variables | Enable |  |  | FALSE |  | FALSE
SV1 | IN208 | Trip Coil 1 Alarm | SELogic Variables | Alarm |  |  | FALSE |  | TRUE
SV1PU | 30 | Trip Coil 1 Alarm | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV1DO | 0 | Trip Coil 1 Alarm | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV2 | IN209 | Trip Coil 2 Alarm | SELogic Variables | Alarm |  |  | FALSE |  | TRUE
SV2PU | 30 | Trip Coil 2 Alarm | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV2DO | 0 | Trip Coil 2 Alarm | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV3 | 0 | Not Used | SELogic Variables | Inactive |  |  | FALSE |  | FALSE
SV3PU | 0 | Not Used | SELogic Variables | Inactive |  |  | TRUE |  | FALSE
SV3DO | 0 | Not Used | SELogic Variables | Inactive |  |  | TRUE |  | FALSE
SV4 | LT4*!(PB1+PB2+PB3+PB4+PB5+PB6+PB7+PB8+PB9+PB10) | Pushbutton Lock | SELogic Variables | Supervisory |  |  | FALSE |  | FALSE
SV4PU | 18000 | Pushbutton Lock | SELogic Variables | Supervisory |  |  | TRUE |  | FALSE
SV4DO | 0 | Pushbutton Lock | SELogic Variables | Supervisory |  |  | TRUE |  | FALSE
SV5 | !(SV1T+SV2T+!LT2*SV6T+!LT2*SV7T+!IN204+IN205+!IN214+!IN215+!IN216) | Close Permissive. Block on TCM, dead bus, and breaker alarms | SELogic Variables | Supervisory |  |  | FALSE |  | FALSE
SV5PU | 0 | Close Permissive. Block on TCM, dead bus, and breaker alarms | SELogic Variables | Supervisory |  |  | TRUE |  | FALSE
SV5DO | 0 | Close Permissive. Block on TCM, dead bus, and breaker alarms | SELogic Variables | Supervisory |  |  | TRUE |  | FALSE
SV6 | 27A1+27B1+27C1 | Level 1 Undervoltage Trip | SELogic Variables | V/Freq Protection |  |  | FALSE |  | TRUE
SV6PU | 660 | Level 1 Undervoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV6DO | 0 | Level 1 Undervoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV7 | 0 | Level 2 Undervoltage Trip | SELogic Variables | V/Freq Protection |  |  | FALSE |  | FALSE
SV7 | 27A2+27B2+27C2 | Level 2 Undervoltage Trip | SELogic Variables | V/Freq Protection |  |  | FALSE |  | TRUE
SV7PU | 0 | Level 2 Undervoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV7DO | 0 | Level 2 Undervoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV8 | 59A1+59B1+59C1 | Level 1 Overvoltage Trip | SELogic Variables | V/Freq Protection |  |  | FALSE |  | TRUE
SV8PU | 42 | Level 1 Overvoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV8DO | 0 | Level 1 Overvoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV9 | 59A2+59B2+59C2 | Level 2 Overvoltage Trip | SELogic Variables | V/Freq Protection |  |  | FALSE |  | TRUE
SV9PU | 150 | Level 2 Overvoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV9DO | 0 | Level 2 Overvoltage Trip | SELogic Variables | V/Freq Protection |  |  | TRUE |  | FALSE
SV10 | !IN105*IN106 | 86BFMV Trip Coil Alarm | SELogic Variables | Alarm |  | 1 | FALSE |  | TRUE
SV10 | 0 | Not Used | SELogic Variables | Inactive |  | 2 | FALSE |  | FALSE
SV10PU | 30 | 86BFMV Trip Coil Alarm | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV10DO | 0 | 86BFMV Trip Coil Alarm | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV11 | OC*LT1 | SCADA Open | SELogic Variables | Control |  |  | FALSE |  | TRUE
SV11PU | 0 | SCADA Open | SELogic Variables | Control |  |  | TRUE |  | FALSE
SV11DO | 30 | SCADA Open | SELogic Variables | Control |  |  | TRUE |  | FALSE
SV12 | CC*LT1 | SCADA Close | SELogic Variables | Control |  |  | FALSE |  | TRUE
SV12PU | 0 | SCADA Close | SELogic Variables | Control |  |  | TRUE |  | FALSE
SV12DO | 30 | SCADA Close | SELogic Variables | Control |  |  | TRUE |  | FALSE
SET1 | !LT1*PB1*LT4 | Remote Enable | Latch Bits | Supervisory |  |  | FALSE |  | TRUE
RST1 | LT1*PB1*LT4 | Remote Enable | Latch Bits | Supervisory |  |  | FALSE |  | FALSE
SET2 | !LT2*PB2*LT4 | Undervoltage Trip Disable | Latch Bits | Supervisory |  |  | FALSE |  | TRUE
RST2 | LT2*PB2*LT4 | Undervoltage Trip Disable | Latch Bits | Supervisory |  |  | FALSE |  | FALSE
SET3 | !LT3*PB3*LT4 | Breaker Failure Disable | Latch Bits | Supervisory |  |  | FALSE |  | TRUE
RST3 | LT3*PB3*LT4 | Breaker Failure Disable | Latch Bits | Supervisory |  |  | FALSE |  | FALSE
SET4 | !LT4*PB5 | Pushbutton Lock | Latch Bits | Supervisory |  |  | FALSE |  | TRUE
RST4 | LT4*(PB5+/SV4T) | Pushbutton Lock | Latch Bits | Supervisory |  |  | FALSE |  | FALSE
SET5 | BFTRIP | Breaker Failed Alarm | Latch Bits | Breaker Failure |  |  | FALSE |  | TRUE
RST5 | !BFTRIP*PB4*LT4 | Breaker Failed Alarm | Latch Bits | Breaker Failure |  |  | FALSE |  | FALSE
SET6 | SV1T | Trip Coil 1 Alarm | Latch Bits | Alarm |  |  | FALSE |  | TRUE
RST6 | !SV1T*LT4*PB6 | Trip Coil 1 Alarm | Latch Bits | Alarm |  |  | FALSE |  | FALSE
SET7 | SV2T | Trip Coil 2 Alarm | Latch Bits | Alarm |  |  | FALSE |  | TRUE
RST7 | !SV2T*LT4*PB6 | Trip Coil 2 Alarm | Latch Bits | Alarm |  |  | FALSE |  | FALSE
SET8 | !LT8*PB7*LT4 | Maintenance Mode | Latch Bits | Maintenance Mode |  |  | FALSE |  | TRUE
RST8 | LT8*PB7*LT4 | Maintenance Mode | Latch Bits | Maintenance Mode |  |  | FALSE |  | FALSE
SET9 | SV6T+SV7T+SV8T+SV9T | Voltage Trip Indication | Latch Bits | Alarm |  |  | FALSE |  | TRUE
RST9 | RB1+TRGTR | Voltage Trip Indication | Latch Bits | Alarm |  |  | FALSE |  | FALSE
SET10 | 81D1T+81D2T | Frequency Trip Indication | Latch Bits | Alarm |  |  | FALSE |  | TRUE
RST10 | RB1+TRGTR | Frequency Trip Indication | Latch Bits | Alarm |  |  | FALSE |  | FALSE
SET11 | SV10T | 86BFMV Trip Coil Alarm | Latch Bits | Alarm |  | 1 | FALSE |  | TRUE
RST11 | !SV10T*LT4*PB6 | 86BFMV Trip Coil Alarm | Latch Bits | Alarm |  | 1 | FALSE |  | FALSE
SET11 | 0 | Not Used | Latch Bits | Inactive |  | 2 | FALSE |  | FALSE
RST11 | 0 | Not Used | Latch Bits | Inactive |  | 2 | FALSE |  | FALSE
OUT101 | TRIP | 52F Protection Trip | Output Contacts | Trip |  |  | FALSE |  | TRUE
OUT102 | SV11T | SCADA Open | Output Contacts | Trip |  |  | FALSE |  | TRUE
OUT103 | SV12T | SCADA Close | Output Contacts | Close |  |  | FALSE |  | TRUE
OUT104 | BFTRIP+LT5 | Breaker Failure Trip | Output Contacts | Breaker Failure |  |  | FALSE |  | TRUE
OUT105 | TRIP+BFTRIP | Fault Indicator | Output Contacts | Alarm |  |  | FALSE |  | FALSE
OUT106 | RT | 52F Backup Trip | Output Contacts | Trip |  |  | FALSE |  | TRUE
OUT107 | SV5T | Permit Close | Output Contacts | Close |  |  | FALSE |  | TRUE
ALRMOUT | !(SALARM+HALARM) | Relay Alarm. Normally closed, held open | Output Contacts | Alarm |  |  | FALSE |  | FALSE
DP1 | IN105 | 86BF Lockout Status | Display Points | Alarm |  |  | FALSE |  | FALSE
DP1_1 | 86BF LOCKOUT | 86BF Lockout Status | Display Points | Alarm |  |  | FALSE |  | FALSE
DP1_0 | NA | 86BF Lockout Status | Display Points | Alarm |  |  | FALSE |  | FALSE
DP2 | IN205+IN206+IN207 | Breaker 27DC Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP2_1 | 52 DC ALARM | Breaker 27DC Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP2_0 | NA | Breaker 27DC Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP3 | IN204 | Breaker Spring Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP3_1 | 52 SPRING ALARM | Breaker Spring Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP3_0 | NA | Breaker Spring Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP4 | IN210 | Breaker Local Remote Status | Display Points | Alarm |  |  | FALSE |  | FALSE
DP4_1 | 52 IN LOCAL | Breaker Local Remote Status | Display Points | Alarm |  |  | FALSE |  | FALSE
DP4_0 | 52 IN REMOTE | Breaker Local Remote Status | Display Points | Alarm |  |  | FALSE |  | FALSE
DP5 | IN202 | Loss of AC Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP5_1 | 52 AC ALM | Loss of AC Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP5_0 | NA | Loss of AC Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP6 | LT9 | Voltage Trip Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP6_1 | VOLT TRIP | Voltage Trip Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP6_0 | NA | Voltage Trip Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP7 | LT10 | Frequency Trip Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP7_1 | FREQ TRIP | Frequency Trip Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP7_0 | NA | Frequency Trip Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP8 | LT6 | Trip Coil 1 Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP8_1 | TCM1 FAIL | Trip Coil 1 Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP8_0 | NA | Trip Coil 1 Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP9 | LT7 | Trip Coil 2 Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP9_1 | TCM2 FAIL | Trip Coil 2 Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP9_0 | NA | Trip Coil 2 Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP10 | LT11 | Lockout Trip Coil Failed Alarm | Display Points | Alarm |  | 1 | FALSE |  | FALSE
DP10 | 0 | Not Used | Display Points | Inactive |  | 2 | FALSE |  | FALSE
DP10_1 | 86TCM FAIL | Lockout Trip Coil Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP10_0 | NA | Lockout Trip Coil Failed Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP11 | IN214 | Loss of DC Close Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP11_1 | NA | Loss of DC Close Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP11_0 | 74DC CL ALM | Loss of DC Close Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP12 | IN215 | Loss of DC Trip 1 Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP12_1 | NA | Loss of DC Trip 1 Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP12_0 | 74DC T1 ALM | Loss of DC Trip 1 Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP13 | IN216 | Loss of DC Trip 2 Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP13_1 | NA | Loss of DC Trip 2 Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP13_0 | 74DC T2 ALM | Loss of DC Trip 2 Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
SS1 | 1 | Settings Group 1 Enable | Settings Group Enable | Enable |  |  | FALSE |  | TRUE
SS2 | 0 | Settings Group 2 Enable | Settings Group Enable | Enable |  |  | FALSE |  | FALSE
SS3 | 0 | Settings Group 3 Enable | Settings Group Enable | Enable |  |  | FALSE |  | FALSE
SS4 | 0 | Settings Group 4 Enable | Settings Group Enable | Enable |  |  | FALSE |  | FALSE
SS5 | 0 | Settings Group 5 Enable | Settings Group Enable | Enable |  |  | FALSE |  | FALSE
SS6 | 0 | Settings Group 6 Enable | Settings Group Enable | Enable |  |  | FALSE |  | FALSE
LED1 | LT1 | Remote Enable | LED | Indication |  |  | FALSE |  | FALSE
LED2 | LT2 | Undervoltage Disable | LED | Indication |  |  | FALSE |  | FALSE
LED3 | LT3 | Breaker Failure Disable | LED | Indication |  |  | FALSE |  | FALSE
LED4 | LT5 | Breaker Failed | LED | Indication |  |  | FALSE |  | FALSE
LED5 | !LT4 | Operator Lock | LED | Indication |  |  | FALSE |  | FALSE
LED6 | LT6+LT7+LT11 | Trip Coil Failed | LED | Indication |  | 1 | FALSE |  | FALSE
LED6 | LT6+LT7 | Trip Coil Failed | LED | Indication |  | 2 | FALSE |  | FALSE
LED7 | LT8 | Maintenance Mode | LED | Indication |  |  | FALSE |  | FALSE
LED8 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED9 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED10 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED12 | TRIP | Trip | LED | Indication |  |  | FALSE |  | FALSE
LED12L | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED13 | 51P1+51G1 | OC Pickup | LED | Indication |  |  | FALSE |  | FALSE
LED13L | N | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED14 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED14L | N | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED15 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED15L | N | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED16 | 67P1T+67P2T+67P3T+67G1T | OC Trip | LED | Indication |  |  | FALSE |  | FALSE
LED16L | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED17 | 51P1T+51G1T | TOC Trip | LED | Indication |  |  | FALSE |  | FALSE
LED17L | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED18 | 81D1T+81D2T | Frequency Trip | LED | Indication |  |  | FALSE |  | FALSE
LED18L | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED19 | !LT2*(SV6T+SV7T) | Undervoltage Trip | LED | Indication |  |  | FALSE |  | FALSE
LED19L | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED20 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED20L | N | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED21 | SV8T+SV9T | Overvoltage Trip | LED | Indication |  |  | FALSE |  | FALSE
LED21L | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED25 | 51G1T+67G1T | Ground Trip | LED | Indication |  |  | FALSE |  | FALSE
LED25L | Y | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
LED26 | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
LED26L | N | LED Latch | LED | Indication |  |  | FALSE |  | FALSE
ER | /67P1+/67P2+/67P3+/51P1+/67G1+/51G1+/SV6+/SV7+/SV8+/SV9+/81D1+/81D2+/52A+\52A | Event Report Triggers | Recording | Trigger |  |  | FALSE |  | FALSE
RSTTRGT | RB1 | Target Reset Equation | Reset | Control |  |  | FALSE |  | FALSE
E50P | 2 | PH OC Enable | Protection Setpoint | Enable |  |  | FALSE |  | FALSE
E51P | 1 | PH TOC Enable | Protection Setpoint | Enable |  |  | FALSE |  | FALSE
E50G | 1 | GND OC Enable | Protection Setpoint | Enable |  |  | FALSE |  | FALSE
E51G | 1 | GND TOC Enable | Protection Setpoint | Enable |  |  | FALSE |  | FALSE
50P1P | 8.55 | Level 1 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | TRUE
50P1P | 11.4 | Level 1 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
50P1P | 0 | Level 1 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
50P1P | 0 | Level 1 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
50P1P | 0 | Level 1 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67P1D | 5 | Level 1 PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
67P1D | 5 | Level 1 PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
67P1D | 0 | Level 1 PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
67P1D | 0 | Level 1 PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
67P1D | 0 | Level 1 PH OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67P1TC | 1 | Level 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
67P1TC | 1 | Level 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
67P1TC | 0 | Level 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
67P1TC | 0 | Level 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
67P1TC | 0 | Level 1 PH OC Torque Control | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
50P2P | 0.25 | Level 2 PH OC Pickup, Maint. Mode (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | TRUE
50P2P | 0.25 | Level 2 PH OC Pickup, Maint. Mode (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
50P2P | 0 | Level 2 PH OC Pickup, Maint. Mode (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
50P2P | 0 | Level 2 PH OC Pickup, Maint. Mode (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
50P2P | 0 | Level 2 PH OC Pickup, Maint. Mode (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67P2D | 0 | Level 2 PH OC Delay, Maint. Mode (cyc) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
67P2D | 0 | Level 2 PH OC Delay, Maint. Mode (cyc) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
67P2D | 0 | Level 2 PH OC Delay, Maint. Mode (cyc) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
67P2D | 0 | Level 2 PH OC Delay, Maint. Mode (cyc) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
67P2D | 0 | Level 2 PH OC Delay, Maint. Mode (cyc) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67P2TC | LT8 | Level 2 PH OC Torque Control, Maint. Mode | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
67P2TC | LT8 | Level 2 PH OC Torque Control, Maint. Mode | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
67P2TC | 0 | Level 2 PH OC Torque Control, Maint. Mode | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
67P2TC | 0 | Level 2 PH OC Torque Control, Maint. Mode | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
67P2TC | 0 | Level 2 PH OC Torque Control, Maint. Mode | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51P1P | 2.03 | Level 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | TRUE
51P1P | 2.71 | Level 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51P1P | 0 | Level 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51P1P | 0 | Level 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51P1P | 0 | Level 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51P1C | U3 | Level 1 PH TOC Curve | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51P1C | U3 | Level 1 PH TOC Curve | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51P1C | 0 | Level 1 PH TOC Curve | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51P1C | 0 | Level 1 PH TOC Curve | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51P1C | 0 | Level 1 PH TOC Curve | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51P1TD | 1 | Level 1 PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
51P1TD | 1 | Level 1 PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51P1TD | 0 | Level 1 PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51P1TD | 0 | Level 1 PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51P1TD | 0 | Level 1 PH TOC Time Dial | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51P1MR | 5 | Level 1 PH TOC Min Response (cyc) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
51P1MR | 5 | Level 1 PH TOC Min Response (cyc) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51P1MR | 0 | Level 1 PH TOC Min Response (cyc) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51P1MR | 0 | Level 1 PH TOC Min Response (cyc) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51P1MR | 0 | Level 1 PH TOC Min Response (cyc) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51P1TC | 1 | Level 1 PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51P1TC | 1 | Level 1 PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51P1TC | 0 | Level 1 PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51P1TC | 0 | Level 1 PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51P1TC | 0 | Level 1 PH TOC Torque Control | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
50G1P | 1.42 | Level 1 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | TRUE
50G1P | 1.9 | Level 1 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
50G1P | 0 | Level 1 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
50G1P | 0 | Level 1 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
50G1P | 0 | Level 1 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67G1D | 5 | Level 1 GND OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
67G1D | 5 | Level 1 GND OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
67G1D | 0 | Level 1 GND OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
67G1D | 0 | Level 1 GND OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
67G1D | 0 | Level 1 GND OC Delay (cyc) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
67G1TC | 1 | Level 1 GND OC Torque Control | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
67G1TC | 1 | Level 1 GND OC Torque Control | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
67G1TC | 0 | Level 1 GND OC Torque Control | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
67G1TC | 0 | Level 1 GND OC Torque Control | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
67G1TC | 0 | Level 1 GND OC Torque Control | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51G1P | 0.61 | Level 1 GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | TRUE
51G1P | 0.81 | Level 1 GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51G1P | 0 | Level 1 GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51G1P | 0 | Level 1 GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51G1P | 0 | Level 1 GND TOC Pickup (A-sec) | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51G1C | U3 | Level 1 GND TOC Curve | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51G1C | U3 | Level 1 GND TOC Curve | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51G1C | 0 | Level 1 GND TOC Curve | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51G1C | 0 | Level 1 GND TOC Curve | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51G1C | 0 | Level 1 GND TOC Curve | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
51G1TD | 1 | Level 1 GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | A |  | TRUE |  | FALSE
51G1TD | 1 | Level 1 GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | B |  | TRUE |  | FALSE
51G1TD | 0 | Level 1 GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | C |  | TRUE |  | FALSE
51G1TD | 0 | Level 1 GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | D |  | TRUE |  | FALSE
51G1TD | 0 | Level 1 GND TOC Time Dial | Protection Setpoint | Overcurrent Protection | E |  | TRUE |  | FALSE
51G1TC | 1 | Level 1 GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | A |  | FALSE |  | FALSE
51G1TC | 1 | Level 1 GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | B |  | FALSE |  | FALSE
51G1TC | 0 | Level 1 GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | C |  | FALSE |  | FALSE
51G1TC | 0 | Level 1 GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | D |  | FALSE |  | FALSE
51G1TC | 0 | Level 1 GND TOC Torque Control | Protection Setpoint | Overcurrent Protection | E |  | FALSE |  | FALSE
E81 | 2 | Enable Frequency Elements | Frequency | Enable |  |  | FALSE |  | FALSE
27B81P | 44.488 | Frequency Undervoltage Block (67% VnomLN) | Frequency | V/Freq Protection |  |  | TRUE |  | FALSE
81D1P | 56.3 | Underfrequency Level 1 (Hz) | Frequency | V/Freq Protection |  |  | TRUE |  | FALSE
81D1D | 3659.5 | Underfrequency Level 1 Time Delay (cyc) | Frequency | V/Freq Protection |  |  | TRUE |  | FALSE
81D2P | 63.5 | Overfrequency Level 1 (Hz) | Frequency | V/Freq Protection |  |  | TRUE |  | FALSE
81D2D | 4127.5 | Overfrequency Level 1 Time Delay (cyc) | Frequency | V/Freq Protection |  |  | TRUE |  | FALSE
EVOLT | Y | Enable Voltage Elements | Voltage | Enable |  |  | FALSE |  | FALSE
27P1P | 55.112 | Undervoltage Level 1 | Voltage | V/Freq Protection |  |  | TRUE |  | FALSE
27P2P | OFF | Undervoltage Level 2 | Voltage | V/Freq Protection |  |  | TRUE |  | FALSE
59P1P | 84.328 | Overvoltage Level 1 | Voltage | V/Freq Protection |  |  | TRUE |  | FALSE
59P2P | 81.008 | Overvoltage Level 2 | Voltage | V/Freq Protection |  |  | TRUE |  | FALSE
EPORT | Y | Enable Port F | Communications | Port F |  |  | FALSE | PF | FALSE
PROTO | SEL | Protocol | Communications | Port F |  |  | FALSE | PF | FALSE
MAXACC | C | Max Access Level | Communications | Port F |  |  | FALSE | PF | FALSE
SPEED | 19200 | Baud Rate | Communications | Port F |  |  | FALSE | PF | FALSE
BITS | 8 | Data Bits | Communications | Port F |  |  | FALSE | PF | FALSE
PARITY | N | Parity | Communications | Port F |  |  | FALSE | PF | FALSE
STOP | 1 | Stop Bits | Communications | Port F |  |  | FALSE | PF | FALSE
FASTOP | Y | Fast Operate Enable | Communications | Port F |  |  | FALSE | PF | FALSE
EPORT | N | Enable Port 1 | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EPORT | N | Enable Port 2 | Communications | Port 2 |  |  | FALSE | P2 | FALSE
EPORT | N | Enable Port 3 | Communications | Port 3 |  |  | FALSE | P3 | FALSE
EPORT | Y | Enable Port 5 | Communications | Port 5 |  |  | FALSE | P5 | FALSE
SUBNETM | 255.255.255.0 | Subnet Mask | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DEFRTR | 172.31.100.254 | Default Router | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ETELNET | Y | Enable Telnet | Communications | Port 5 |  |  | FALSE | P5 | FALSE
TPORT | 23 | Telnet Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
FASTOP | Y | Fast Operate Enable | Communications | Port 5 |  |  | FALSE | P5 | FALSE
EDNP | 2 | Enable DNP Sessions | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPNUM | 20000 | DNP Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPADR | 1 | DNP Server Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPIP1 | 172.31.100.241 | DNP Client IP Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPTR1 | TCP | DNP Transport Protocol | Communications | Port 5 |  |  | FALSE | P5 | FALSE
REPADR1 | 0 | DNP Client Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPMAP1 | 1 | DNP Session Map | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DVARAI1 | 5 | AI Default Variation | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLA1 | 0 | Current Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLV1 | 0 | Volt Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLM1 | 0 | Misc Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBA1 | 0 | Amps Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBV1 | 0 | Volts Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBM1 | 0 | Misc Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPIP2 | 172.31.100.243 | DNP Client IP Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPTR2 | TCP | DNP Transport Protocol | Communications | Port 5 |  |  | FALSE | P5 | FALSE
REPADR2 | 0 | DNP Client Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPMAP2 | 1 | DNP Session Map | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DVARAI2 | 5 | AI Default Variation | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLA2 | 0 | Current Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLV2 | 0 | Volt Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLM2 | 0 | Misc Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBA2 | 0 | Amps Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBV2 | 0 | Volts Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBM2 | 0 | Misc Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
BI_000 | TIRIG | IRIG Status | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_001 | LED1 | Remote Enable | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_002 | LED2 | Undervoltage Disable | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_003 | LED3 | Breaker Failure Disable | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_004 | LED4 | Breaker Failure | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_005 | LED5 | Operator Lock | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_006 | LED6 | Trip Coil Failed | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_007 | LED7 | Maintenance Mode | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_008 | LED8 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_009 | LED9 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_010 | LED10 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_011 | TLED11 | Relay Enabled | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_012 | TLED12 | Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_013 | TLED13 | Overcurrent Pickup | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_014 | TLED14 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_015 | TLED15 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_016 | TLED16 | Instantaneous Overcurrent Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_017 | TLED17 | Time Overcurrent Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_018 | TLED18 | Frequency Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_019 | TLED19 | Undervoltage Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_020 | TLED20 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_021 | TLED21 | Overvoltage Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_022 | TLED22 | A Phase Involved | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_023 | TLED23 | B Phase Involved | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_024 | TLED24 | C Phase Involved | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_025 | TLED25 | Ground Involved | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_026 | TLED26 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_027 | IN101 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_028 | IN102 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_029 | IN105 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_030 | IN106 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_031 | IN202 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_032 | IN203 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_033 | IN204 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_034 | IN205 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_035 | IN206 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_036 | IN207 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_037 | IN208 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_038 | IN209 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_039 | IN210 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_040 | IN211 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_041 | IN214 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_042 | IN215 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_043 | IN216 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_044 | OUT107 | IO | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_045 | LT6 | Trip Coil Alarm T1 | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_046 | LT7 | Trip Coil Alarm T2 | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_047 | LT11 | Trip Coil Alarm 86 | Communications | DNP 1 |  | 1 | FALSE | D1 | FALSE
BI_029 | IN202 | IO | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
BI_030 | IN203 | IO | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
BI_031 | IN204 | IO | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
BI_032 | IN205 | IO | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
BI_033 | IN206 | IO | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
BI_034 | IN207 | IO | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
BI_035 | IN208 | IO | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
BI_036 | IN209 | IO | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
BI_037 | IN210 | IO | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
BI_038 | IN211 | IO | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
BI_039 | IN214 | IO | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
BI_040 | IN215 | IO | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
BI_041 | IN216 | IO | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
BI_042 | OUT107 | IO | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
BI_043 | LT6 | Trip Coil Alarm T1 | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
BI_044 | LT7 | Trip Coil Alarm T2 | Communications | DNP 1 |  | 2 | FALSE | D1 | FALSE
AI_000 | IA | Current A | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_001 | IB | Current B | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_002 | IC | Current C | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_003 | IG | Current G | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_004 | VA | Voltage A | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_005 | VB | Voltage B | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_006 | VC | Voltage C | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_007 | VAB | Voltage AB | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_008 | VBC | Voltage BC | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_009 | VCA | Voltage CA | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_010 | MW3 | Real Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_011 | MVAR3 | Reactive Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_012 | FREQ | Frequency | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_013 | VDC | Battery Voltage | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_000 | RB1 | Target Reset | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_001 | OC | Breaker Open | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_002 | CC | Breaker Close | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
SER1 | TRIP,CLOSE,SV1T,SV2T,SV6T,SV7T,SV8T,SV9T,SV10T,SV11T,SV12T,LT1,LT2,LT3,LT4,LT5,LT6,LT7,LT8,LT9,LT10,LT11 | SER1 Trigger List (24 Elements Max) | Report | SER |  |  | FALSE |  | TRUE
SER2 | IN101,IN102,IN105,IN106,IN204,IN205,IN206,IN207,IN208,IN209,IN214,IN215,IN216,OUT101,OUT102,OUT103,OUT104,OUT106,OUT107,ALARM,OC,CC,RB1 | SER2 Trigger List (24 Elements Max) | Report | SER |  |  | FALSE |  | TRUE
SER3 | SG1,50P1,67P1T,50P2,67P2T,51P1,51P1T,50G1,67G1T,51G1,51G1T | SER3 Trigger List (24 Elements Max) | Report | SER |  |  | FALSE |  | TRUE

## CAP_487V
SEL-487V Cap Bank Protection Settings & Logic
Relay Specification
Manufacturer | SEL
Model | SEL-487V
Part # | 0487V1X4151XB0X4H5B444X
Function | Cap Bank Protection
Front View |  |  |  | Rear View
Relay Classification
Relay ID (RID) | Setpoint Class | Logic Class | IP Address/CIDR (IPADDR)
11C1 | A | 2 | 172.31.100.90/24
I/O Summary |  |  | Remote Bit Summary
I/O | Description |  | Element | Description | Behavior
IN101 | 52C1 Status (a) |  | RB01 | 52C1 Remote Open | Pulse
IN102 | 52C1 Status (b) |  | RB02 | 52C1 Remote Close | Pulse
IN103 | 86CSW1 TCM |  | RB03 | CSW1 Auto Open | Pulse
IN104 | 86CSW2 TCM |  | RB04 | CSW1 Auto Close | Pulse
IN105 | Not Used |  | RB05 | CSW1 Remote Open | Pulse
IN106 | Not Used |  | RB06 | CSW1 Remote Close | Pulse
IN107 | Not Used |  | RB07 | CSW2 Auto Open | Pulse
OUT101 | 52C1 Protection Trip |  | RB08 | CSW2 Auto Close | Pulse
OUT102 | 52C1 SCADA Trip |  | RB09 | CSW2 Remote Open | Pulse
OUT103 | 52C1 SCADA Close |  | RB10 | CSW2 Remote Close | Pulse
OUT104 | 86BFL1 Trip |  | RB11 | CSW3 Auto Open | Pulse
OUT105 | 52C1 Block Close |  | RB12 | CSW3 Auto Close | Pulse
OUT106 | 52C1 Secondary Trip |  | RB13 | CSW3 Remote Open | Pulse
OUT107 | Not Used |  | RB14 | CSW3 Remote Close | Pulse
OUT108 | Relay Fail Alarm (NC) |  | RB15 | Target Reset | Pulse
IN201 | 74 DC 52C1 Close
IN202 | 74 DC 52C1 Trip 1
IN203 | 74 DC 52C1 Trip 2 |  | Pushbutton Summary
IN204 | 52C1 Loss of AC Heater |  | Element | Description | Target LED
IN205 | 52C1 Loss of AC Motor |  | PB1 | 52C1 Remote Enable | PB1_LED
IN206 | 52C1 Spring Alarm |  | PB2 | Undervoltage Disable | PB2_LED
IN207 | 52C1 Loss of DC Close |  | PB3 | Breaker Failure Disable | PB3_LED
IN208 | 52C1 Loss of DC Trip 1 |  | PB4 | Breaker Failed (push to reset) | PB4_LED
IN209 | 52C1 Loss of DC Trip 2 |  | PB5 | Trip Coil Failed (push to reset) | PB5_LED
IN210 | 52C1 Trip 1 TCM |  | PB6 | Operator Lock (hold to disable) | PB6_LED
IN211 | 52C1 Trip 2 TCM |  | PB7 | CAP Unbalance Alarm (push to reset) | PB7_LED
IN212 | 52C1 43L/R Indication |  | PB8 | Auto Control Enable | PB8_LED
IN213 | 74 DC CSW1 Close Circuit |  | PB9 | CSW1 Auto/Remote Enable | PB9_LED
IN214 | 74 DC CSW1 Trip Circuit |  | PB10 | CSW2 Auto/Remote Enable | PB10_LED
IN215 | 86CSW1 Status |  | PB11 | Not Used | PB11_LED
IN216 | CSW1 Status (a) |  | PB12 | Not Used | PB12_LED
IN217 | CSW1 Status (b)
IN218 | CSW1 Loss of AC
IN219 | CSW1 Loss of DC
IN220 | CSW1 Low SF6 Alarm
IN221 | CSW1 Low SF6 Lockout
IN222 | CSW1 Spring Alarm
IN223 | CSW1 43L/R Indication
IN224 | CSW1 TCM
OUT201 | 86CSW1 Trip
OUT202 | CSW1 Trip
OUT203 | CSW1 Close
OUT204 | CSW1 Block Close
IN301 | 74 DC CSW2 Close Circuit
IN302 | 74 DC CSW2 Trip Circuit
IN303 | 86CSW2 Status
IN304 | CSW2 Status (a)
IN305 | CSW2 Status (b)
IN306 | CSW2 Loss of AC
IN307 | CSW2 Loss of DC
IN308 | CSW2 Low SF6 Alarm
IN309 | CSW2 Low SF6 Lockout
IN310 | CSW2 Spring Alarm
IN311 | CSW2 43L/R Indication
IN312 | CSW2 TCM
IN313 | Not Used
IN314 | Not Used
IN315 | Not Used
IN316 | Not Used
IN317 | Not Used
IN318 | Not Used
IN319 | Not Used
IN320 | Not Used
IN321 | Not Used
IN322 | Not Used
IN323 | Not Used
IN324 | Not Used
OUT301 | 86CSW2 Trip
OUT302 | CSW2 Trip
OUT303 | CSW2 Close
OUT304 | CSW2 Block Close
OUT305 | Not Used
OUT306 | Not Used
OUT307 | Not Used
OUT308 | Not Used
Ratios & Cap Ratings |  | Setpoint Class
Terminal | Element | A | B | C | D | E
W | CTRW | 240
| MV Voltage (kV-LL) | 34.5
Y | PTRY | 300
Y | VNOMY (V-sec, LL) | 115
CAP Neutral Voltage
Z | PTRZ1 | 175
Z | PTRZ2
Z | PTRZ3
CAP Ratings (Mvar)
| Stage 1 | 11
| Stage 2 | 11
Short Circuit Current Magnitudes
Relay | Fault Location | 3PH (A-pri) | SLG/2PH-G 3I0 (A-pri)
11C1 | CAP BUS 1 | 20937.0134 | 12399.1368
Cap Bank Unbalance Voltages
Faulty Units | 0 | 1 | 2 | 3
Primary Neutral-Gnd Voltage | 0 | 686.85 | 1422.76 | 2213.18
Secondary Neutral-Gnd Voltage | 0 | 3.92 | 8.13 | 12.65
Primary Manufacturer Recommended Setpoint | 0
Secondary Manufacturer Recommended Setpoint | 0
Voltage on Affected Phase | 19920 | 20607 | 21343 | 22133
Ground Diff Voltage Settings |  | Setpoint Class
Stage 1 Unbalance Alarm (80% of 1-Unit Fault Unbalance) |  | A | B | C | D | E
Pickup | 87AG1P (V-sec) | 3.14
Delay | 87AG1PU (cyc) | 5
Stage 1 Level 1 Unbalance (80% of 2-Unit Fault Unbalance)
Pickup | 87TG1P (V-sec) | 6.5
Delay | 87TG1PU (cyc) | 1
Stage 1 Level 2 Unbalance (80% of 3-Unit Fault Unbalance)
Pickup | 87HG1P (V-sec) | 10.12
Delay | 87HG1PU (cyc) | 0.17
Stage 2 Unbalance Alarm (80% of 1-Unit Fault Unbalance)
Pickup | 87AG2P (V-sec) | 3.14
Delay | 87AG2PU (cyc) | 5
Stage 2 Level 1 Unbalance (80% of 2-Unit Fault Unbalance)
Pickup | 87TG2P (V-sec) | 6.5
Delay | 87TG2PU (cyc) | 1
Stage 2 Level 2 Unbalance (80% of 3-Unit Fault Unbalance)
Pickup | 87HG2P (V-sec) | 10.12
Delay | 87HG2PU (cyc) | 0.17
Instantaneous PH OC Settings |  | Setpoint Class
Level 1 |  | A | B | C | D | E
Cap Bank FLA | A-pri | 368.1654
Min 3PH Fault | A-pri | 20937.0134
Pickup | 50WP1P (A-sec) | 6.14
Delay | 50WP1D (cyc) | 0
Level 2 (BF Detector) |  | A | B | C | D | E
Pickup | 50WP2P (A-sec) | 3.07
Delay | 50WP2D (cyc) | 0
Instantaneous PH OC Philosophy
Level 1 phase instantaneous pickups are set above 400% of the capacitor bank’s maximum operating current magnitude and below the three-phase fault magnitude. A 400% margin is selected to ride-through switching transients. The level 2 phase instantaneous element is used as a breaker failure detector and is set to 50% of the level 1 phase time overcurrent pickup. No intentional delays are included.
Inverse TOC Settings |  | Setpoint Class
Level 1 Phase (Inverse TOC Element 1) |  | A | B | C | D | E
Cap Bank FLA |  | 368.1654
Operate Quantity | 51O01 | IMAXWF
Pickup | 51P01 (A-sec) | 1.9942
Curve | 51C01 | U3
Time Dial | 51TD01 | 1
Torque Control | 51TC01 | 1
Level 1 Ground (Inverse TOC Element 2) |  | A | B | C | D | E
Operate Quantity | 51O02 | 3I0WM
Pickup | 51P02 (A-sec) | 0.2301
Curve | 51C02 | U3
Time Dial | 51TD02 | 1
Torque Control | 51TC02 | 1
Inverse TOC Philosophy
Level 1 phase time overcurrent pickup is set equal to 130% of the capacitor bank’s maximum operating current. The level 1 ground time overcurrent pickup is set equal to 30% of the FLA for a single cap bank stage. No downstream coordination is required, and the time dial is selected to coordinate with upstream protection as needed.
Residual GND OC Settings |  | Setpoint Class
Level 1 |  | A | B | C | D | E
Pickup | 50WG1P (A-sec) | 1.842
Delay | 50WG1D (cyc) | 0
Level 2 (BF Dectector) |  | A | B | C | D | E
Pickup | 50WG2P (A-sec) | 0.25
Delay | 50WG2D (cyc) | 0
GND OC Philosophy
Level 1 residual ground overcurrent pickups are set equal to 50% of 50WP1P. The level 2 residual ground element is used as a breaker failure detection element and the pickup is set equal to the ground time overcurrent pickup or minimum setting range, whichever is greatest. No intentional delay will be added.
Voltage Settings
Description | Pickup |  | Pickup Delay |  | Operate Quantity
| Element | Value | Logic | Cycles | Element | Logic
Undervolt (40% OF VnomL-N) | 27P1P1 (V) | 46 | 27P1D1 (cyc) | 300 | 27O1 | VNMINYF
Overvolt (115% OF VnomL-N) | 59P1P1 (V) | 132.25 | 59P1D1 (cyc) | 60 | 59O1 | VNMAXYF
The table above summarizes the active 11C under/over voltage protection.
Settings Table
Setting | Value | Description | Category | Function | Setpoint Class | Logic Class | Float | QuickSet Group | SER
SID | GRVR HL WND | Station Identifier | Global | General |  |  | FALSE |  | FALSE
NFREQ | 60 | Nominal Frequency (Hz) | Global | General |  |  | FALSE |  | FALSE
PHROT | ABC | Phase Rotation | Global | General |  |  | FALSE |  | FALSE
SS1 | 1 | Settings Group 1 Enable | Global | Enable |  |  | FALSE |  | FALSE
FRQST | Y | Primary Frequency Source Terminal | Global | General |  |  | FALSE |  | FALSE
RSTTRGT | RB15 | Target Reset | Global | Control |  |  | FALSE |  | FALSE
UTCOFF | -5 | UTC Offset to Local Time | Global | Time |  |  | TRUE |  | FALSE
EPMU | N | Enable PMU | Global | PMU |  |  | FALSE |  | FALSE
MFRMT | C37.118 | Message Format | Global | PMU |  |  | FALSE |  | FALSE
MRATE | 60 | Messages per Second | Global | PMU |  |  | FALSE |  | FALSE
PMAPP | N | Type of PMU Application | Global | PMU |  |  | FALSE |  | FALSE
PMLEGCY | Y | Enable Legacy Settings | Global | PMU |  |  | FALSE |  | FALSE
PMID | 1 | PMU Hardware ID | Global | PMU |  |  | FALSE |  | FALSE
PHVOLT | Y | Include Voltage Terminal | Global | PMU |  |  | FALSE |  | FALSE
PHCURR | W | Include Current Terminal | Global | PMU |  |  | FALSE |  | FALSE
PHDATAV | ALL | Phasor Data Set Voltages | Global | PMU |  |  | FALSE |  | FALSE
PHDATAI | ALL | Phasor Data Set Currents | Global | PMU |  |  | FALSE |  | FALSE
PHNR | F | PMU Float or Integer | Global | PMU |  |  | FALSE |  | FALSE
PHFMT | P | Phasor Format Polar or Rectangular | Global | PMU |  |  | FALSE |  | FALSE
FNR | F | Freq Format Float or Integer | Global | PMU |  |  | FALSE |  | FALSE
SRATE | 2 | Sample Rate of Event Report (kHz) | Report | Event |  |  | FALSE |  | FALSE
LER | 2 | Length of Event Report (Seconds) | Report | Event |  |  | TRUE |  | FALSE
PRE | 0.25 | Length of Pre-Fault (Seconds) | Report | Event |  |  | TRUE |  | FALSE
ECAPAP | UNGNDV | Capacitor Bank Application: Ungrounded Capacitor Bank | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E50 | W | Enable OC | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E51 | 2 | Enable TOC (#) | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E59 | 1 | Enable Overvolt (#) | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E27 | 1 | Enable Undervolt (#) | Relay Configuration | Enable |  |  | FALSE |  | FALSE
CTRW | 240 | Terminal W CT Ratio | Current and Potential Transformer Data | Ratio |  |  | FALSE |  | FALSE
PTRY | 300 | Terminal Y PT Ratio | Current and Potential Transformer Data | Ratio |  |  | TRUE |  | FALSE
PTRZ1 | 175 | Terminal Z1 PT Ratio | Current and Potential Transformer Data | Ratio |  |  | TRUE |  | FALSE
PTRZ2 | 1 | Terminal Z2 PT Ratio | Current and Potential Transformer Data | Ratio |  |  | TRUE |  | FALSE
PTRZ3 | 1 | Terminal Z3 PT Ratio | Current and Potential Transformer Data | Ratio |  |  | TRUE |  | FALSE
VNOMY | 115 | Terminal Y Nominal LL Voltage (V-sec) | Current and Potential Transformer Data | Ratio |  |  | TRUE |  | FALSE
VNOMZ | 110 | Terminal Z Nominal LL Voltage (V-sec), DEFUALT VALUE - NOT USED | Current and Potential Transformer Data | Ratio |  |  | TRUE |  | FALSE
E87G | G1 | Enable Ground Diff Volt Elements | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 1 | FALSE |  | FALSE
E87G | G1,G2 | Enable Ground Diff Volt Elements | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 2 | FALSE |  | FALSE
E87G | G1,G2,G3 | Enable Ground Diff Volt Elements | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 3 | FALSE |  | FALSE
87AG1P | 3.14 | Stage 1 Alarm Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff | A |  | TRUE |  | FALSE
87AG1P | 0 | Stage 1 Alarm Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff | B |  | TRUE |  | FALSE
87AG1P | 0 | Stage 1 Alarm Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff | C |  | TRUE |  | FALSE
87AG1PU | 5 | Stage 1 Alarm Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff | A |  | TRUE |  | FALSE
87AG1PU | 0 | Stage 1 Alarm Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff | B |  | TRUE |  | FALSE
87AG1PU | 0 | Stage 1 Alarm Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff | C |  | TRUE |  | FALSE
87TG1P | 6.5 | Stage 1 Trip Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff | A |  | TRUE |  | FALSE
87TG1P | 0 | Stage 1 Trip Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff | B |  | TRUE |  | FALSE
87TG1P | 0 | Stage 1 Trip Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff | C |  | TRUE |  | FALSE
87TG1PU | 1 | Stage 1 Trip Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff | A |  | TRUE |  | FALSE
87TG1PU | 0 | Stage 1 Trip Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff | B |  | TRUE |  | FALSE
87TG1PU | 0 | Stage 1 Trip Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff | C |  | TRUE |  | FALSE
87HG1P | 10.12 | Stage 1 High Trip Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff | A |  | TRUE |  | FALSE
87HG1P | 0 | Stage 1 High Trip Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff | B |  | TRUE |  | FALSE
87HG1P | 0 | Stage 1 High Trip Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff | C |  | TRUE |  | FALSE
87HG1PU | 0.17 | Stage 1 High Trip Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff | A |  | TRUE |  | FALSE
87HG1PU | 0 | Stage 1 High Trip Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff | B |  | TRUE |  | FALSE
87HG1PU | 0 | Stage 1 High Trip Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff | C |  | TRUE |  | FALSE
87AG1EN | IN216 | CAP1: Alarm Enable. CapSwitcher must be closed. | Ungrounded Bank Differential Voltage Elements | Bank Diff |  |  | FALSE |  | FALSE
87TG1EN | IN216 | CAP1: Trip Enable. CapSwitcher must be closed. | Ungrounded Bank Differential Voltage Elements | Bank Diff |  |  | FALSE |  | FALSE
87HG1EN | IN216 | CAP1: High Trip Enable. CapSwitcher must be closed. | Ungrounded Bank Differential Voltage Elements | Bank Diff |  |  | FALSE |  | FALSE
87G1F | Y | CAP1: Capacitor bank is externally fused. | Ungrounded Bank Differential Voltage Elements | Bank Diff |  |  | FALSE |  | FALSE
87AG2P | 0 | Stage 2 Alarm Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff | B |  | TRUE |  | FALSE
87AG2P | 0 | Stage 2 Alarm Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff | C |  | TRUE |  | FALSE
87AG2PU | 0 | Stage 2 Alarm Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff | B |  | TRUE |  | FALSE
87AG2PU | 0 | Stage 2 Alarm Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff | C |  | TRUE |  | FALSE
87TG2P | 0 | Stage 2 Trip Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff | B |  | TRUE |  | FALSE
87TG2P | 0 | Stage 2 Trip Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff | C |  | TRUE |  | FALSE
87TG2PU | 0 | Stage 2 Trip Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff | B |  | TRUE |  | FALSE
87TG2PU | 0 | Stage 2 Trip Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff | C |  | TRUE |  | FALSE
87HG2P | 0 | Stage 2 High Trip Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff | B |  | TRUE |  | FALSE
87HG2P | 0 | Stage 2 High Trip Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff | C |  | TRUE |  | FALSE
87HG2PU | 0 | Stage 2 High Trip Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff | B |  | TRUE |  | FALSE
87HG2PU | 0 | Stage 2 High Trip Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff | C |  | TRUE |  | FALSE
87AG2EN | IN304 | CAP2: Alarm Enable. CapSwitcher must be closed. | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 2,3 | FALSE |  | FALSE
87TG2EN | IN304 | CAP2: Trip Enable. CapSwitcher must be closed. | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 2,3 | FALSE |  | FALSE
87HG2EN | IN304 | CAP2: High Trip Enable. CapSwitcher must be closed. | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 2,3 | FALSE |  | FALSE
87G2F | Y | CAP2: Capacitor bank is externally fused. | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 2,3 | FALSE |  | FALSE
87AG3P | #REF! | Stage 3 Alarm Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 3 | TRUE |  | FALSE
87AG3PU | #REF! | Stage 3 Alarm Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 3 | TRUE |  | FALSE
87TG3P | #REF! | Stage 3 Trip Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 3 | TRUE |  | FALSE
87TG3PU | #REF! | Stage 3 Trip Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 3 | TRUE |  | FALSE
87HG3P | #REF! | Stage 3 High Trip Pickup (V-sec) | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 3 | TRUE |  | FALSE
87HG3PU | #REF! | Stage 3 High Trip Delay (cyc) | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 3 | TRUE |  | FALSE
87AG3EN | IN316 | CAP3: Alarm Enable. CapSwitcher must be closed. | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 3 | FALSE |  | FALSE
87TG3EN | IN316 | CAP3: Trip Enable. CapSwitcher must be closed. | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 3 | FALSE |  | FALSE
87HG3EN | IN316 | CAP3: High Trip Enable. CapSwitcher must be closed. | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 3 | FALSE |  | FALSE
87G3F | Y | CAP3: Capacitor bank is externally fused. | Ungrounded Bank Differential Voltage Elements | Bank Diff |  | 3 | FALSE |  | FALSE
E50W | P,G | Enable Terminal W OC Types |  |  |  |  | FALSE |  | FALSE
50WP1P | 6.14 | Level 1 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent | A |  | TRUE |  | FALSE
50WP1P |  | Level 1 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent | B |  | TRUE |  | FALSE
50WP1P |  | Level 1 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent | C |  | TRUE |  | FALSE
50WP1D | 0 | Level 1 PH OC Delay (cyc) | Protection Setpoint | Overcurrent | A |  | TRUE |  | FALSE
50WP1D | 0 | Level 1 PH OC Delay (cyc) | Protection Setpoint | Overcurrent | B |  | TRUE |  | FALSE
50WP1D | 0 | Level 1 PH OC Delay (cyc) | Protection Setpoint | Overcurrent | C |  | TRUE |  | FALSE
50WP2P | 3.07 | Level 2 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent | A |  | TRUE |  | FALSE
50WP2P |  | Level 2 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent | B |  | TRUE |  | FALSE
50WP2P |  | Level 2 PH OC Pickup (A-sec) | Protection Setpoint | Overcurrent | C |  | TRUE |  | FALSE
50WP2D | 0 | Level 2 PH OC Delay (cyc) | Protection Setpoint | Overcurrent | A |  | TRUE |  | FALSE
50WP2D | 0 | Level 2 PH OC Delay (cyc) | Protection Setpoint | Overcurrent | B |  | TRUE |  | FALSE
50WP2D | 0 | Level 2 PH OC Delay (cyc) | Protection Setpoint | Overcurrent | C |  | TRUE |  | FALSE
51O01 | IMAXWF | Level 1 PH TOC Op. Quantity | Protection Setpoint | Overcurrent | A |  | FALSE |  | FALSE
51O01 | 0 | Level 1 PH TOC Op. Quantity | Protection Setpoint | Overcurrent | B |  | FALSE |  | FALSE
51O01 | 0 | Level 1 PH TOC Op. Quantity | Protection Setpoint | Overcurrent | C |  | FALSE |  | FALSE
51P01 | 1.9942 | Level 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent | A |  | TRUE |  | FALSE
51P01 |  | Level 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent | B |  | TRUE |  | FALSE
51P01 |  | Level 1 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent | C |  | TRUE |  | FALSE
51C01 | U3 | Level 1 PH TOC Curve | Protection Setpoint | Overcurrent | A |  | FALSE |  | FALSE
51C01 | 0 | Level 1 PH TOC Curve | Protection Setpoint | Overcurrent | B |  | FALSE |  | FALSE
51C01 | 0 | Level 1 PH TOC Curve | Protection Setpoint | Overcurrent | C |  | FALSE |  | FALSE
51TD01 | 1 | Level 1 PH TOC Time Dial | Protection Setpoint | Overcurrent | A |  | TRUE |  | FALSE
51TD01 | 0 | Level 1 PH TOC Time Dial | Protection Setpoint | Overcurrent | B |  | TRUE |  | FALSE
51TD01 | 0 | Level 1 PH TOC Time Dial | Protection Setpoint | Overcurrent | C |  | TRUE |  | FALSE
51TC01 | 1 | Level 1 PH TOC Torque Control | Protection Setpoint | Overcurrent | A |  | FALSE |  | FALSE
51TC01 | 0 | Level 1 PH TOC Torque Control | Protection Setpoint | Overcurrent | B |  | FALSE |  | FALSE
51TC01 | 0 | Level 1 PH TOC Torque Control | Protection Setpoint | Overcurrent | C |  | FALSE |  | FALSE
51O02 | 3I0WM | Level 2 PH TOC Op. Quantity | Protection Setpoint | Overcurrent | A |  | FALSE |  | FALSE
51O02 | 0 | Level 2 PH TOC Op. Quantity | Protection Setpoint | Overcurrent | B |  | FALSE |  | FALSE
51O02 | 0 | Level 2 PH TOC Op. Quantity | Protection Setpoint | Overcurrent | C |  | FALSE |  | FALSE
51P02 | 0.2301 | Level 2 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent | A |  | TRUE |  | FALSE
51P02 |  | Level 2 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent | B |  | TRUE |  | FALSE
51P02 |  | Level 2 PH TOC Pickup (A-sec) | Protection Setpoint | Overcurrent | C |  | TRUE |  | FALSE
51C02 | U3 | Level 2 PH TOC Curve | Protection Setpoint | Overcurrent | A |  | FALSE |  | FALSE
51C02 | 0 | Level 2 PH TOC Curve | Protection Setpoint | Overcurrent | B |  | FALSE |  | FALSE
51C02 | 0 | Level 2 PH TOC Curve | Protection Setpoint | Overcurrent | C |  | FALSE |  | FALSE
51TD02 | 1 | Level 2 PH TOC Time Dial | Protection Setpoint | Overcurrent | A |  | TRUE |  | FALSE
51TD02 | 0 | Level 2 PH TOC Time Dial | Protection Setpoint | Overcurrent | B |  | TRUE |  | FALSE
51TD02 | 0 | Level 2 PH TOC Time Dial | Protection Setpoint | Overcurrent | C |  | TRUE |  | FALSE
51TC02 | 1 | Level 2 PH TOC Torque Control | Protection Setpoint | Overcurrent | A |  | FALSE |  | FALSE
51TC02 | 0 | Level 2 PH TOC Torque Control | Protection Setpoint | Overcurrent | B |  | FALSE |  | FALSE
51TC02 | 0 | Level 2 PH TOC Torque Control | Protection Setpoint | Overcurrent | C |  | FALSE |  | FALSE
50WG1P | 1.842 | Level 1 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent | A |  | TRUE |  | FALSE
50WG1P |  | Level 1 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent | B |  | TRUE |  | FALSE
50WG1P |  | Level 1 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent | C |  | TRUE |  | FALSE
50WG1D | 0 | Level 1 GND OC Delay (cyc) | Protection Setpoint | Overcurrent | A |  | TRUE |  | FALSE
50WG1D | 0 | Level 1 GND OC Delay (cyc) | Protection Setpoint | Overcurrent | B |  | TRUE |  | FALSE
50WG1D | 0 | Level 1 GND OC Delay (cyc) | Protection Setpoint | Overcurrent | C |  | TRUE |  | FALSE
50WG2P | 0.25 | Level 2 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent | A |  | TRUE |  | FALSE
50WG2P |  | Level 2 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent | B |  | TRUE |  | FALSE
50WG2P |  | Level 2 GND OC Pickup (A-sec) | Protection Setpoint | Overcurrent | C |  | TRUE |  | FALSE
50WG2D | 0 | Level 2 GND OC Delay (cyc) | Protection Setpoint | Overcurrent | A |  | TRUE |  | FALSE
50WG2D | 0 | Level 2 GND OC Delay (cyc) | Protection Setpoint | Overcurrent | B |  | TRUE |  | FALSE
50WG2D | 0 | Level 2 GND OC Delay (cyc) | Protection Setpoint | Overcurrent | C |  | TRUE |  | FALSE
27O1 | VNMINYF | Undervoltage Op. Quantity | Protection Setpoint | Voltage |  |  | FALSE |  | FALSE
27P1P1 | 46 | Undervoltage Pickup (V-sec) | Protection Setpoint | Voltage |  |  | TRUE |  | FALSE
27P1D1 | 300 | Undervoltage Delay (cyc) | Protection Setpoint | Voltage |  |  | TRUE |  | FALSE
59O1 | VNMAXYF | Overvoltage Op. Quantity | Protection Setpoint | Voltage |  |  | FALSE |  | FALSE
59P1P1 | 132.25 | Overvoltage Pickup (V-sec) | Protection Setpoint | Voltage |  |  | TRUE |  | FALSE
59P1D1 | 60 | Overvoltage Delay (cyc) | Protection Setpoint | Voltage |  |  | TRUE |  | FALSE
TRW | 50WP1 OR 50WG1 OR 51T01 OR 51T02 OR (271P1T AND NOT PLT02) OR 591P1T | Trip Medium Voltage Breaker | Trip Logic |  |  |  | FALSE |  | TRUE
ULTRW | NOT IN101 OR TRGTR OR NOT (50WP1 OR 50WG1 OR 51T01 OR 51T02 OR 271P1T OR 591P1T) | Unlatch Trip | Trip Logic |  |  |  | FALSE |  | FALSE
TDURD | 9 | Trip Minimum Duration | Trip Logic |  |  |  | TRUE |  | FALSE
ER | R_TRIG 51S01 OR R_TRIG 51S02 OR R_TRIG 271P1 OR R_TRIG 591P1 OR R_TRIG 87AG1D OR R_TRIG 87AG2D OR R_TRIG 87AG3D OR F_TRIG IN101 OR F_TRIG IN216 OR F_TRIG IN304 | Event Report Trigger | Trip Logic |  |  |  | FALSE |  | FALSE
FAULT | 50WP1 OR 50WG1 OR 51T01 OR 51T02 | Fault Conditions | Trip Logic |  |  |  | FALSE |  | FALSE
PROTSEL1 | PSV01 := PLT10 AND PLT11 AND RB03 # CSW1 Auto Open | CSW1 Auto Open | Variables |  |  |  | FALSE |  | TRUE
PROTSEL2 | PSV02 := PLT10 AND PLT11 AND RB04 # CSW1 Auto Close | CSW1 Auto Close | Variables |  |  |  | FALSE |  | TRUE
PROTSEL3 | PSV03 := NOT PLT10 AND PLT11 AND RB05 # CSW1 SCADA Open | CSW1 SCADA Open | Variables |  |  |  | FALSE |  | TRUE
PROTSEL4 | PSV04 := NOT PLT10 AND PLT11 AND RB06 # CSW1 SCADA Close | CSW1 SCADA Close | Variables |  |  |  | FALSE |  | TRUE
PROTSEL5 | PSV05 := PLT10 AND PLT12 AND RB07 # CSW2 Auto Open | CSW2 Auto Open | Variables |  |  | 2,3 | FALSE |  | TRUE
PROTSEL6 | PSV06 := PLT10 AND PLT12 AND RB08 # CSW2 Auto Close | CSW2 Auto Close | Variables |  |  | 2,3 | FALSE |  | TRUE
PROTSEL7 | PSV07 := NOT PLT10 AND PLT12 AND RB09 # CSW2 SCADA Open | CSW2 SCADA Open | Variables |  |  | 2,3 | FALSE |  | TRUE
PROTSEL8 | PSV08 := NOT PLT10 AND PLT12 AND RB10 # CSW2 SCADA Close | CSW2 SCADA Close | Variables |  |  | 2,3 | FALSE |  | TRUE
PROTSEL9 | PSV09 := PLT10 AND PLT13 AND RB11 # CSW3 Auto Open | CSW3 Auto Open | Variables |  |  | 3 | FALSE |  | TRUE
PROTSEL10 | PSV10 := PLT10 AND PLT13 AND RB12 # CSW3 Auto Close | CSW3 Auto Close | Variables |  |  | 3 | FALSE |  | TRUE
PROTSEL11 | PSV11 := NOT PLT10 AND PLT12 AND RB13 # CSW3 SCADA Open | CSW3 SCADA Open | Variables |  |  | 3 | FALSE |  | TRUE
PROTSEL12 | PSV12 := NOT PLT10 AND PLT12 AND RB14 # CSW3 SCADA Close | CSW3 SCADA Close | Variables |  |  | 3 | FALSE |  | TRUE
PROTSEL13 | PSV13 := (PSV13 OR TRIP) AND (50WP2 OR 50WG2) # 52C1 Breaker Failure | 52C1 Breaker Failure | Variables |  |  |  | FALSE |  | TRUE
PROTSEL14 | # | [5 empty] | FALSE |  | FALSE
PROTSEL15 | # | [5 empty] | FALSE |  | FALSE
PROTSEL16 | ########################### # | [5 empty] | FALSE |  | FALSE
PROTSEL17 | PCT01DO := 9.0 # Breaker Failure Timer | Breaker Failure Timer | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL18 | PCT01PU := 9.0 # Breaker Failure Timer | Breaker Failure Timer | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL19 | PCT01IN := NOT PLT03 AND PSV13 # Breaker Failure Timer | Breaker Failure Timer | Timed Variables |  |  |  | FALSE |  | TRUE
PROTSEL20 | PCT02DO := 0.0 # 86CSW1 Trip Coil Failure | 86CSW1 Trip Coil Failure | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL21 | PCT02PU := 30.0 # 86CSW1 Trip Coil Failure | 86CSW1 Trip Coil Failure | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL22 | PCT02IN := IN103 AND NOT IN215 # 86CSW1 Trip Coil Failure | 86CSW1 Trip Coil Failure | Timed Variables |  |  |  | FALSE |  | TRUE
PROTSEL23 | PCT03DO := 0.0 # 86CSW2 Trip Coil Failure | 86CSW2 Trip Coil Failure | Timed Variables |  |  | 2,3 | FALSE |  | FALSE
PROTSEL24 | PCT03PU := 30.0 # 86CSW2 Trip Coil Failure | 86CSW2 Trip Coil Failure | Timed Variables |  |  | 2,3 | FALSE |  | FALSE
PROTSEL25 | PCT03IN := IN104 AND NOT IN303 # 86CSW2 Trip Coil Failure | 86CSW2 Trip Coil Failure | Timed Variables |  |  | 2,3 | FALSE |  | TRUE
PROTSEL26 | PCT04DO := 0.0 # 86CSW3 Trip Coil Failure | 86CSW3 Trip Coil Failure | Timed Variables |  |  | 3 | FALSE |  | FALSE
PROTSEL27 | PCT04PU := 30.0 # 86CSW3 Trip Coil Failure | 86CSW3 Trip Coil Failure | Timed Variables |  |  | 3 | FALSE |  | FALSE
PROTSEL28 | PCT04IN := IN105 AND NOT IN315 # 86CSW3 Trip Coil Failure | 86CSW3 Trip Coil Failure | Timed Variables |  |  | 3 | FALSE |  | TRUE
PROTSEL29 | PCT05DO := 0.0 # 52C1 TCM1 (SEL-2652) | 52C1 TCM1 (SEL-2652) | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL30 | PCT05PU := 30.0 # 52C1 TCM1 (SEL-2652) | 52C1 TCM1 (SEL-2652) | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL31 | PCT05IN := IN210 # 52C1 TCM1 (SEL-2652) | 52C1 TCM1 (SEL-2652) | Timed Variables |  |  |  | FALSE |  | TRUE
PROTSEL32 | PCT06DO := 0.0 # 52C1 TCM2 (SEL-2652) | 52C1 TCM2 (SEL-2652) | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL33 | PCT06PU := 30.0 # 52C1 TCM2 (SEL-2652) | 52C1 TCM2 (SEL-2652) | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL34 | PCT06IN := IN211 # 52C1 TCM2 (SEL-2652) | 52C1 TCM2 (SEL-2652) | Timed Variables |  |  |  | FALSE |  | TRUE
PROTSEL35 | PCT07DO := 0.0 # CSW1 TCM | CSW1 TCM | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL36 | PCT07PU := 30.0 # CSW1 TCM | CSW1 TCM | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL37 | PCT07IN := IN224 AND IN216 # CSW1 TCM | CSW1 TCM | Timed Variables |  |  |  | FALSE |  | TRUE
PROTSEL38 | PCT08DO := 0.0 # CSW2 TCM | CSW2 TCM | Timed Variables |  |  | 2,3 | FALSE |  | FALSE
PROTSEL39 | PCT08PU := 30.0 # CSW2 TCM | CSW2 TCM | Timed Variables |  |  | 2,3 | FALSE |  | FALSE
PROTSEL40 | PCT08IN := IN312 AND IN304 # CSW2 TCM | CSW2 TCM | Timed Variables |  |  | 2,3 | FALSE |  | TRUE
PROTSEL41 | PCT09DO := 0.0 # CSW3 TCM | CSW3 TCM | Timed Variables |  |  | 3 | FALSE |  | FALSE
PROTSEL42 | PCT09PU := 30.0 # CSW3 TCM | CSW3 TCM | Timed Variables |  |  | 3 | FALSE |  | FALSE
PROTSEL43 | PCT09IN := IN324 AND IN316 # CSW3 TCM | CSW3 TCM | Timed Variables |  |  | 3 | FALSE |  | TRUE
PROTSEL44 | PCT10DO := 0.0 # Pushbutton Unlock | Pushbutton Unlock | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL45 | PCT10PU := 180.0 # Pushbutton Unlock | Pushbutton Unlock | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL46 | PCT10IN := PB6 # Pushbutton Unlock | Pushbutton Unlock | Timed Variables |  |  |  | FALSE |  | TRUE
PROTSEL47 | PCT11DO := 0.0 # Pushbutton Auto-Lock | Pushbutton Auto-Lock | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL48 | PCT11PU := 18000.0 # Pushbutton Auto-Lock | Pushbutton Auto-Lock | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL49 | PCT11IN := PLT06 AND NOT (PB1 OR PB2 OR PB3 OR PB4 OR PB5 OR PB6 OR PB7 OR PB8 OR PB9 OR PB10 OR PB11 OR PB12) # Pushbutton Auto-Lock | Pushbutton Auto-Lock | Timed Variables |  |  |  | FALSE |  | TRUE
PROTSEL50 | PCT12DO := 18000.0 # CAPA Discharge Timer | CAP1 Discharge Timer | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL51 | PCT12PU := 0.0 # CAPA Discharge Timer | CAP1 Discharge Timer | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL52 | PCT12IN := F_TRIG IN216 # CAPA Discharge Timer | CAP1 Discharge Timer | Timed Variables |  |  |  | FALSE |  | TRUE
PROTSEL53 | PCT13DO := 18000.0 # CAPB Discharge Timer | CAP2 Discharge Timer | Timed Variables |  |  | 2,3 | FALSE |  | FALSE
PROTSEL54 | PCT13PU := 0.0 # CAPB Discharge Timer | CAP2 Discharge Timer | Timed Variables |  |  | 2,3 | FALSE |  | FALSE
PROTSEL55 | PCT13IN := F_TRIG IN304 # CAPB Discharge Timer | CAP2 Discharge Timer | Timed Variables |  |  | 2,3 | FALSE |  | TRUE
PROTSEL56 | PCT14DO := 18000.0 # CAPC Discharge Timer | CAP3 Discharge Timer | Timed Variables |  |  | 3 | FALSE |  | FALSE
PROTSEL57 | PCT14PU := 0.0 # CAPC Discharge Timer | CAP3 Discharge Timer | Timed Variables |  |  | 3 | FALSE |  | FALSE
PROTSEL58 | PCT14IN := F_TRIG IN316 # CAPC Discharge Timer | CAP3 Discharge Timer | Timed Variables |  |  | 3 | FALSE |  | TRUE
PROTSEL59 | PCT15DO := 20.0 # 52T Interlock | 52T Interlock | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL60 | PCT15PU := 0.0 # 52T Interlock | 52T Interlock | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL61 | PCT15IN := F_TRIG IN214 # 52T Interlock | 52T Interlock | Timed Variables |  |  |  | FALSE |  | TRUE
PROTSEL62 | PCT16DO := 20.0 # 52C1 Interlock | 52C1 Interlock | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL63 | PCT16PU := 0.0 # 52C1 Interlock | 52C1 Interlock | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL64 | PCT16IN := F_TRIG IN101 # 52C1 Interlock | 52C1 Interlock | Timed Variables |  |  |  | FALSE |  | TRUE
PROTSEL65 | PCT17DO := 20.0 # 52C1 SCADA Open | 52C1 SCADA Open | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL66 | PCT17PU := 0.0 # 52C1 SCADA Open | 52C1 SCADA Open | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL67 | PCT17IN := PLT01 AND RB01 # 52C1 SCADA Open | 52C1 SCADA Open | Timed Variables |  |  |  | FALSE |  | TRUE
PROTSEL68 | PCT18DO := 20.0 # 52C1 SCADA Close | 52C1 SCADA Close | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL69 | PCT18PU := 0.0 # 52C1 SCADA Close | 52C1 SCADA Close | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL70 | PCT18IN := PLT01 AND RB02 # 52C1 SCADA Close | 52C1 SCADA Close | Timed Variables |  |  |  | FALSE |  | TRUE
PROTSEL71 | PCT19DO := 20.0 # CSW1 Open | CSW1 Open | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL72 | PCT19PU := 0.0 # CSW1 Open | CSW1 Open | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL73 | PCT19IN := PSV01 OR PSV03 # CSW1 Open | CSW1 Open | Timed Variables |  |  |  | FALSE |  | TRUE
PROTSEL74 | PCT20DO := 20.0 # CSW1 Close | CSW1 Close | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL75 | PCT20PU := 0.0 # CSW1 Close | CSW1 Close | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL76 | PCT20IN := PSV02 OR PSV04 # CSW1 Close | CSW1 Close | Timed Variables |  |  |  | FALSE |  | TRUE
PROTSEL77 | PCT21DO := 20.0 # CSW2 Open | CSW2 Open | Timed Variables |  |  | 2,3 | FALSE |  | FALSE
PROTSEL78 | PCT21PU := 0.0 # CSW2 Open | CSW2 Open | Timed Variables |  |  | 2,3 | FALSE |  | FALSE
PROTSEL79 | PCT21IN := PSV05 OR PSV07 # CSW2 Open | CSW2 Open | Timed Variables |  |  | 2,3 | FALSE |  | TRUE
PROTSEL80 | PCT22DO := 20.0 # CSW2 Close | CSW2 Close | Timed Variables |  |  | 2,3 | FALSE |  | FALSE
PROTSEL81 | PCT22PU := 0.0 # CSW2 Close | CSW2 Close | Timed Variables |  |  | 2,3 | FALSE |  | FALSE
PROTSEL82 | PCT22IN := PSV06 OR PSV08 # CSW2 Close | CSW2 Close | Timed Variables |  |  | 2,3 | FALSE |  | TRUE
PROTSEL83 | PCT23DO := 20.0 # CSW3 Open | CSW3 Open | Timed Variables |  |  | 3 | FALSE |  | FALSE
PROTSEL84 | PCT23PU := 0.0 # CSW3 Open | CSW3 Open | Timed Variables |  |  | 3 | FALSE |  | FALSE
PROTSEL85 | PCT23IN := PSV09 OR PSV11 # CSW3 Open | CSW3 Open | Timed Variables |  |  | 3 | FALSE |  | TRUE
PROTSEL86 | PCT24DO := 20.0 # CSW3 Close | CSW3 Close | Timed Variables |  |  | 3 | FALSE |  | FALSE
PROTSEL87 | PCT24PU := 0.0 # CSW3 Close | CSW3 Close | Timed Variables |  |  | 3 | FALSE |  | FALSE
PROTSEL88 | PCT24IN := PSV10 OR PSV12 # CSW3 Close | CSW3 Close | Timed Variables |  |  | 3 | FALSE |  | TRUE
PROTSEL89 | PCT25DO := 9.0 # 52C1 Retrip Timer | 52C1 Retrip Timer | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL90 | PCT25PU := 4.0 # 52C1 Retrip Timer | 52C1 Retrip Timer | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL91 | PCT25IN := (PCT25Q OR (TRIP AND IN101)) AND (50WP2 OR 50WG2) # 52C1 Retrip Timer | 52C1 Retrip Timer | Timed Variables |  |  |  | FALSE |  | TRUE
PROTSEL92 | PCT26PU :=0 # Remote Operation Indication | Remote Operation Indication | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL93 | PCT26DO :=180 # Remote Operation Indication | Remote Operation Indication | Timed Variables |  |  |  | FALSE |  | FALSE
PROTSEL94 | PCT26IN :=PSV01 OR PSV02 OR PSV03 OR PSV04 # Remote Operation Indication | Remote Operation Indication | Timed Variables |  |  | 1 | FALSE |  | TRUE
PROTSEL94 | PCT26IN :=PSV01 OR PSV02 OR PSV03 OR PSV04 OR PSV05 OR PSV06 OR PSV07 OR PSV08 # Remote Operation Indication | Remote Operation Indication | Timed Variables |  |  | 2 | FALSE |  | TRUE
PROTSEL94 | PCT26IN :=PSV01 OR PSV02 OR PSV03 OR PSV04 OR PSV05 OR PSV06 OR PSV07 OR PSV08 OR PSV09 OR PSV10 OR PSV11 OR PSV12 # Remote Operation Indication | Remote Operation Indication | Timed Variables |  |  | 3 | FALSE |  | TRUE
PROTSEL95 | ############################ # | [5 empty] | FALSE |  | FALSE
PROTSEL96 | PLT01S := NOT PLT01 AND PB1_PUL AND PLT06 # Remote Enable | 52C1 Remote Enable | Latches |  |  |  | FALSE |  | TRUE
PROTSEL97 | PLT01R := PLT01 AND PB1_PUL AND PLT06 # Remote Enable | 52C1 Remote Enable | Latches |  |  |  | FALSE |  | FALSE
PROTSEL98 | PLT02S := NOT PLT02 AND PB2_PUL AND PLT06 # Undervoltage Disable | Undervoltage Disable | Latches |  |  |  | FALSE |  | TRUE
PROTSEL99 | PLT02R := PLT02 AND PB2_PUL AND PLT06 # Undervoltage Disable | Undervoltage Disable | Latches |  |  |  | FALSE |  | FALSE
PROTSEL100 | PLT03S := NOT PLT03 AND PB3_PUL # Breaker Failure Disable | Breaker Failure Disable | Latches |  |  |  | FALSE |  | TRUE
PROTSEL101 | PLT03R := PLT03 AND PB3_PUL AND PLT06 # Breaker Failure Disable | Breaker Failure Disable | Latches |  |  |  | FALSE |  | FALSE
PROTSEL102 | PLT04S := PCT01Q # Breaker Failure | Breaker Failure | Latches |  |  |  | FALSE |  | TRUE
PROTSEL103 | PLT04R :=PB4_PUL AND PLT06 # Breaker Failure | Breaker Failure | Latches |  |  |  | FALSE |  | FALSE
PROTSEL104 | PLT05S := PCT02Q OR PCT05Q OR PCT06Q OR PCT07Q # Trip Coil Failure | Trip Coil Failure | Latches |  |  | 1 | FALSE |  | TRUE
PROTSEL104 | PLT05S := PCT02Q OR PCT03Q OR PCT05Q OR PCT06Q OR PCT07Q OR PCT08Q # Trip Coil Failure | Trip Coil Failure | Latches |  |  | 2 | FALSE |  | TRUE
PROTSEL104 | PLT05S := PCT02Q OR PCT03Q OR PCT04Q OR PCT05Q OR PCT06Q OR PCT07Q OR PCT08Q OR PCT09Q # Trip Coil Failure | Trip Coil Failure | Latches |  |  | 3 | FALSE |  | TRUE
PROTSEL105 | PLT05R :=PB5_PUL AND PLT06 # Trip Coil Failure | Trip Coil Failure | Latches |  |  |  | FALSE |  | FALSE
PROTSEL106 | PLT06S := PCT10Q # Pushbutton Operator Lock Disable | Pushbutton Operator Lock Disable | Latches |  |  |  | FALSE |  | TRUE
PROTSEL107 | PLT06R :=PB6_PUL OR PCT11Q # Pushbutton Operator Lock Disable | Pushbutton Operator Lock Disable | Latches |  |  |  | FALSE |  | FALSE
PROTSEL108 | PLT07S := 87AG1D # Cap A Unbalance Alarm | Cap 1 Unbalance Alarm | Latches |  |  |  | FALSE |  | TRUE
PROTSEL109 | PLT07R :=PB7_PUL AND PLT06 # Cap A Unbalance Alarm | Cap 1 Unbalance Alarm | Latches |  |  |  | FALSE |  | FALSE
PROTSEL110 | PLT08S := 87AG2D # Cap B Unbalance Alarm | Cap 2 Unbalance Alarm | Latches |  |  | 2,3 | FALSE |  | TRUE
PROTSEL111 | PLT08R :=PB7_PUL AND PLT06 # Cap B Unbalance Alarm | Cap 2 Unbalance Alarm | Latches |  |  | 2,3 | FALSE |  | FALSE
PROTSEL112 | PLT09S := 87AG3D # Cap C Unbalance Alarm | Cap 3 Unbalance Alarm | Latches |  |  | 3 | FALSE |  | TRUE
PROTSEL113 | PLT09R :=PB7_PUL AND PLT06 # Cap C Unbalance Alarm | Cap 3 Unbalance Alarm | Latches |  |  | 3 | FALSE |  | FALSE
PROTSEL114 | PLT10S := NOT PLT10 AND PB8_PUL AND PLT06 # Auto Control Enable | Auto Control Enable | Latches |  |  |  | FALSE |  | TRUE
PROTSEL115 | PLT10R := PLT10 AND PB8_PUL AND PLT06 # Auto Control Enable | Auto Control Enable | Latches |  |  |  | FALSE |  | FALSE
PROTSEL116 | PLT11S := NOT PLT11 AND PB9_PUL AND PLT06 # CSW1 Auto/SCADA Enable | CSW1 Auto/SCADA Enable | Latches |  |  |  | FALSE |  | TRUE
PROTSEL117 | PLT11R := PLT11 AND PB9_PUL AND PLT06 # CSW1 Auto/SCADA Enable | CSW1 Auto/SCADA Enable | Latches |  |  |  | FALSE |  | FALSE
PROTSEL118 | PLT12S := NOT PLT12 AND PB10PUL AND PLT06 # CSW2 Auto/SCADA Enable | CSW2 Auto/SCADA Enable | Latches |  |  | 2,3 | FALSE |  | TRUE
PROTSEL119 | PLT12R := PLT12 AND PB10PUL AND PLT06 # CSW2 Auto/SCADA Enable | CSW2 Auto/SCADA Enable | Latches |  |  | 2,3 | FALSE |  | FALSE
PROTSEL120 | PLT13S := NOT PLT13 AND PB11PUL AND PLT06 # CSW3 Auto/SCADA Enable | CSW3 Auto/SCADA Enable | Latches |  |  | 3 | FALSE |  | TRUE
PROTSEL121 | PLT13R := PLT13 AND PB11PUL AND PLT06 # CSW3 Auto/SCADA Enable | CSW3 Auto/SCADA Enable | Latches |  |  | 3 | FALSE |  | FALSE
AUTO_1 | ASV100 := ACN01Q OR ACN02Q OR ACN03Q # Operation Counter Reset | Operation Counter Reset | Automation Variables |  |  |  | FALSE |  | FALSE
AUTO_2 | ASV101 := IN216 # CSW1 Operation Counter Input | CSW1 Operation Counter Input | Automation Variables |  |  |  | FALSE |  | FALSE
AUTO_3 | ASV102 := IN304 # CSW2 Operation Counter Input | CSW2 Operation Counter Input | Automation Variables |  |  | 2,3 | FALSE |  | FALSE
AUTO_4 | ASV103 := IN316 # CSW3 Operation Counter Input | CSW3 Operation Counter Input | Automation Variables |  |  | 3 | FALSE |  | FALSE
AUTO_5 | ASV104 := 0 # |  | Automation Variables |  |  |  | FALSE |  | FALSE
AUTO_6 | ASV105 := 0 # |  | Automation Variables |  |  |  | FALSE |  | FALSE
AUTO_7 | ASV106 := 0 # |  | Automation Variables |  |  |  | FALSE |  | FALSE
AUTO_8 | ASV107 := 0 # |  | Automation Variables |  |  |  | FALSE |  | FALSE
AUTO_9 | ASV108 := 0 # |  | Automation Variables |  |  |  | FALSE |  | FALSE
AUTO_10 | ASV109 := 0 # |  | Automation Variables |  |  |  | FALSE |  | FALSE
AUTO_11 | ASV110 := NOT (87TG1D OR 87HG1D OR PCT12Q OR PCT07Q OR IN215) AND IN101 # CAP1 Availability NOT Unbalance or Discharging or Bad Trip Coil or Lockout AND 52C1 Closed | CAP1 Availability NOT Unbalance or Discharging or Bad Trip Coil or Lockout AND 52C1 Closed | Automation Variables |  |  |  | FALSE |  | FALSE
AUTO_12 | ASV111 := NOT (87TG2D OR 87HG2D OR PCT13Q OR PCT08Q OR IN303) AND IN101 # CAP2 Availability NOT Unbalance or Discharging or Bad Trip Coil or Lockout AND 52C1 Closed | CAP2 Availability NOT Unbalance or Discharging or Bad Trip Coil or Lockout AND 52C1 Closed | Automation Variables |  |  | 2,3 | FALSE |  | FALSE
AUTO_13 | ASV112 := NOT (87TG3D OR 87HG3D OR PCT14Q OR PCT09Q OR IN315) AND IN101 # CAP3 Availability NOT Unbalance or Discharging or Bad Trip Coil or Lockout AND 52C1 Closed | CAP3 Availability NOT Unbalance or Discharging or Bad Trip Coil or Lockout AND 52C1 Closed | Automation Variables |  |  | 3 | FALSE |  | FALSE
AUTO_14 | # | [5 empty] | FALSE |  | FALSE
AUTO_15 | # | [5 empty] | FALSE |  | FALSE
AUTO_16 | # | [5 empty] | FALSE |  | FALSE
AUTO_17 | ############################ # | [5 empty] | FALSE |  | FALSE
AUTO_18 | ACN01PV :=10000.0 # CSW1 Operation Counter | CSW1 Operation Counter | Automation Counters |  |  |  | FALSE |  | FALSE
AUTO_19 | ACN01R :=ASV100 # CSW1 Operation Counter Reset | CSW1 Operation Counter Reset | Automation Counters |  |  |  | FALSE |  | FALSE
AUTO_20 | ACN01IN :=ASV101 # CSW1 Operation Counter Input | CSW1 Operation Counter Input | Automation Counters |  |  |  | FALSE |  | FALSE
AUTO_21 | ACN02PV :=10000.0 # CSW2 Operation Counter | CSW2 Operation Counter | Automation Counters |  |  | 2,3 | FALSE |  | FALSE
AUTO_22 | ACN02R :=ASV100 # CSW2 Operation Counter Reset | CSW2 Operation Counter Reset | Automation Counters |  |  | 2,3 | FALSE |  | FALSE
AUTO_23 | ACN02IN :=ASV102 # CSW2 Operation Counter Input | CSW2 Operation Counter Input | Automation Counters |  |  | 2,3 | FALSE |  | FALSE
AUTO_24 | ACN03PV :=10000.0 # CSW3 Operation Counter | CSW3 Operation Counter | Automation Counters |  |  | 3 | FALSE |  | FALSE
AUTO_25 | ACN03R :=ASV100 # CSW3 Operation Counter Reset | CSW3 Operation Counter Reset | Automation Counters |  |  | 3 | FALSE |  | FALSE
AUTO_26 | ACN03IN :=ASV103 # CSW3 Operation Counter Input | CSW3 Operation Counter Input | Automation Counters |  |  | 3 | FALSE |  | FALSE
AUTO_27 | ############################ # | [5 empty] | FALSE |  | FALSE
AUTO_28 | AMV001 :=ACN01CV # CSW1 Operation Counter (SCADA) | CSW1 Operation Counter (SCADA) | Automation Math Variables |  |  |  | FALSE |  | FALSE
AUTO_29 | AMV002 :=ACN02CV # CSW2 Operation Counter (SCADA) | CSW2 Operation Counter (SCADA) | Automation Math Variables |  |  | 2,3 | FALSE |  | FALSE
AUTO_30 | AMV003 :=ACN03CV # CSW3 Operation Counter (SCADA) | CSW3 Operation Counter (SCADA) | Automation Math Variables |  |  | 3 | FALSE |  | FALSE
AUTO_31 | ############################ | [5 empty] | FALSE |  | FALSE
AUTO_32 | AMV004 := VAZFMC*PTRZ1 # CAPA Neutral Voltage | CAP1 Neutral Voltage | Automation Math Variables |  |  |  | FALSE |  | FALSE
AUTO_33 | AMV005 := VBZFMC*PTRZ2 # CAP B Neutral Voltage | CAP2 Neutral Voltage | Automation Math Variables |  |  | 2,3 | FALSE |  | FALSE
AUTO_34 | AMV006 := VCZFMC*PTRZ3 # CAP C Neutral Voltage | CAP3 Neutral Voltage | Automation Math Variables |  |  | 3 | FALSE |  | FALSE
OUT101 | TRW OR PCT15Q | 52C1 Primary Trip, Trip W Conditions or 52T Open | Output Contacts | Trip |  |  | FALSE |  | TRUE
OUT102 | PCT17Q | 52C1 SCADA Open | Output Contacts | Open |  |  | FALSE |  | TRUE
OUT103 | PCT18Q | 52C1 SCADA Close | Output Contacts | Close |  |  | FALSE |  | TRUE
OUT104 | PCT01Q OR PLT04 | 86BFL1 Trip | Output Contacts | Trip |  |  | FALSE |  | TRUE
OUT105 | NOT(PCT05Q OR PLT04) AND IN214 | 52C1 Block Close, Blocks on 52C1 trip coil 1 failed, 52C1 breaker failure, or 52Tx open. | Output Contacts | Block Close |  |  | FALSE |  | TRUE
OUT106 | PCT25Q | 52C1 Backup Trip | Output Contacts | Trip |  |  | FALSE |  | TRUE
OUT107 | 0 | Not Used | Output Contacts |  |  |  | FALSE |  | TRUE
OUT108 | NOT(SALARM OR HALARM) | Relay Failure Alarm. Normally Closed, Held Open | Output Contacts | Alarm |  |  | FALSE |  | TRUE
OUT201 | (87TG1D OR 87HG1D) AND NOT (50WP1 OR 50WG1) | 86CSW1 Trip | Output Contacts | Trip |  |  | FALSE |  | TRUE
OUT202 | (87TG1D OR 87HG1D) AND NOT (50WP1 OR 50WG1) OR PCT01Q OR PCT16Q OR PCT19Q | CSW1 Open/Trip: Opens on cap differential, 52C1 breaker failure, 52C1 status, and auto/remote commands. | Output Contacts | Trip |  |  | FALSE |  | TRUE
OUT203 | PCT20Q | CSW1 Close | Output Contacts | Close |  |  | FALSE |  | TRUE
OUT204 | NOT(PCT12Q OR PCT07Q OR PLT04) AND IN101 | CSW1 Block Close: Blocks on discharge timer, CSW1 trip coil failure, 52C1 breaker failure and 52C1 status. | Output Contacts | Block Close |  |  | FALSE |  | TRUE
OUT301 | (87TG2D OR 87HG2D) AND NOT (50WP1 OR 50WG1) | 86CSW2 Trip | Output Contacts | Trip |  | 2,3 | FALSE |  | TRUE
OUT302 | (87TG2D OR 87HG2D) AND NOT (50WP1 OR 50WG1) OR PCT01Q OR PCT16Q OR PCT21Q | CSW2 Open/Trip: Opens on cap differential, 52C1 breaker failure, 52C1 status, and auto/remote commands. | Output Contacts | Trip |  | 2,3 | FALSE |  | TRUE
OUT303 | PCT22Q | CSW2 Close | Output Contacts | Close |  | 2,3 | FALSE |  | TRUE
OUT304 | NOT(PCT13Q OR PCT08Q OR PLT04) AND IN101 | CSW2 Block Close: Blocks on discharge timer, CSW2 trip coil failure, 52C1 breaker failure and 52C1 status. | Output Contacts | Block Close |  | 2,3 | FALSE |  | TRUE
OUT305 | (87TG3D OR 87HG3D) AND NOT (50WP1 OR 50WG1) | 86CSW3 Trip | Output Contacts | Trip |  | 3 | FALSE |  | TRUE
OUT306 | (87TG3D OR 87HG3D) AND NOT (50WP1 OR 50WG1) OR PCT01Q OR PCT16Q OR PCT23Q | CSW3 Open/Trip: Opens on cap differential, 52C1 breaker failure, 52C1 status, and auto/remote commands. | Output Contacts | Trip |  | 3 | FALSE |  | TRUE
OUT307 | PCT24Q | CSW3 Close | Output Contacts | Close |  | 3 | FALSE |  | TRUE
OUT308 | NOT(PCT14Q OR PCT09Q OR PLT04) AND IN101 | CSW3 Block Close: Blocks on discharge timer, CSW3 trip coil failure, 52C1 breaker failure and 52C1 status. | Output Contacts | Block Close |  | 3 | FALSE |  | TRUE
DP_ELE1 | PCT02Q | CAP1 Lockout Trip Coil Fail | Display Points | Alarm |  |  | FALSE |  | TRUE
DP_SET1 | 86CSW1 TC FAIL | [5 empty] | FALSE |  | FALSE
DP_CLR1 | [6 empty] | FALSE |  | FALSE
DP_ELE2 | PCT03Q | CAP2 Lockout Trip Coil Fail | Display Points | Alarm |  | 2,3 | FALSE |  | FALSE
DP_SET2 | 86CSW2 TC FAIL |  |  |  |  | 2,3 | FALSE |  | FALSE
DP_CLR2 | [6 empty] | FALSE |  | FALSE
DP_ELE3 | PCT04Q | CAP3 Lockout Trip Coil Fail | Display Points | Alarm |  | 3 | FALSE |  | FALSE
DP_SET3 | 86CSW3 TC FAIL |  |  |  |  | 3 | FALSE |  | FALSE
DP_CLR3 | [6 empty] | FALSE |  | FALSE
DP_ELE4 | PCT05Q | Breaker Trip Coil 1 Fail | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET4 | 52C1 TC1 FAIL | [5 empty] | FALSE |  | FALSE
DP_CLR4 | [6 empty] | FALSE |  | FALSE
DP_ELE5 | PCT06Q | Breaker Trip Coil 2 Fail | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET5 | 52C1 TC2 FAIL | [5 empty] | FALSE |  | FALSE
DP_CLR5 | [6 empty] | FALSE |  | FALSE
DP_ELE6 | PCT07Q | CSW1 Trip Coil Fail | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET6 | CSW1 TC FAIL | [5 empty] | FALSE |  | FALSE
DP_CLR6 | [6 empty] | FALSE |  | FALSE
DP_ELE7 | PCT08Q | CSW2 Trip Coil Fail | Display Points | Alarm |  | 2,3 | FALSE |  | FALSE
DP_SET7 | CSW2 TC FAIL |  |  |  |  | 2,3 | FALSE |  | FALSE
DP_CLR7 | [6 empty] | FALSE |  | FALSE
DP_ELE8 | PCT09Q | CSW3 Trip Coil Fail | Display Points | Alarm |  | 3 | FALSE |  | FALSE
DP_SET8 | CSW3 TC FAIL |  |  |  |  | 3 | FALSE |  | FALSE
DP_CLR8 | [6 empty] | FALSE |  | FALSE
DP_ELE9 | AMV001 | CSW1 Operation Counter | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_NAM9 | CSW1 CNTR: | [5 empty] | FALSE |  | FALSE
DP_SET9 | 5 | [5 empty] | FALSE |  | FALSE
DP_SCA9 | 1 | [5 empty] | FALSE |  | FALSE
DP_CLR9 | [6 empty] | FALSE |  | FALSE
DP_ELE10 | AMV002 | CSW2 Operation Counter | Display Points | Alarm |  | 2,3 | FALSE |  | FALSE
DP_NAM10 | CSW2 CNTR: |  |  |  |  | 2,3 | FALSE |  | FALSE
DP_SET10 | 5 |  |  |  |  | 2,3 | FALSE |  | FALSE
DP_SCA10 | 1 |  |  |  |  | 2,3 | FALSE |  | FALSE
DP_CLR10 | [5 empty] | 2,3 | FALSE |  | FALSE
DP_ELE11 | AMV003 | CSW3 Operation Counter | Display Points | Alarm |  | 3 | FALSE |  | FALSE
DP_NAM11 | CSW3 CNTR: |  |  |  |  | 3 | FALSE |  | FALSE
DP_SET11 | 5 |  |  |  |  | 3 | FALSE |  | FALSE
DP_SCA11 | 1 |  |  |  |  | 3 | FALSE |  | FALSE
DP_CLR11 | [5 empty] | 3 | FALSE |  | FALSE
DP_ELE12 | IN201 | 52C1 Loss of Close DC Voltage | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET12 | [6 empty] | FALSE |  | FALSE
DP_CLR12 | 52C1 74CLOSE | [5 empty] | FALSE |  | FALSE
DP_ELE13 | IN202 | 52C1 Loss of Trip 1 DC Voltage | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET13 | [6 empty] | FALSE |  | FALSE
DP_CLR13 | 52C1 74TRIP1 | [5 empty] | FALSE |  | FALSE
DP_ELE14 | IN203 | 52C1 Loss of Trip 2 DC Voltage | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET14 | [6 empty] | FALSE |  | FALSE
DP_CLR14 | 52C1 74TRIP2 | [5 empty] | FALSE |  | FALSE
DP_ELE15 | IN204 | 52C1 Loss of AC Heater | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET15 | [6 empty] | FALSE |  | FALSE
DP_CLR15 | 52C1 HTR ALM | [5 empty] | FALSE |  | FALSE
DP_ELE16 | IN205 | 52C1 Loss of AC Motor | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET16 | [6 empty] | FALSE |  | FALSE
DP_CLR16 | 52C1 MTR ALM | [5 empty] | FALSE |  | FALSE
DP_ELE17 | IN206 | 52C1 Spring Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET17 | [6 empty] | FALSE |  | FALSE
DP_CLR17 | 52C1 SPRNG ALM | [5 empty] | FALSE |  | FALSE
DP_ELE18 | IN207 | 52C1 Loss of DC Close | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET18 | [6 empty] | FALSE |  | FALSE
DP_CLR18 | 52C1 27DC CLOSE | [5 empty] | FALSE |  | FALSE
DP_ELE19 | IN208 | 52C1 Loss of DC Trip 1 | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET19 | [6 empty] | FALSE |  | FALSE
DP_CLR19 | 52C1 27DC TRIP1 | [5 empty] | FALSE |  | FALSE
DP_ELE20 | IN209 | 52C1 Loss of DC Trip 2 | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET20 | [6 empty] | FALSE |  | FALSE
DP_CLR20 | 52C1 27DC TRIP2 | [5 empty] | FALSE |  | FALSE
DP_ELE21 | IN210 | 52C1 TCM Trip 1 | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET21 | [6 empty] | FALSE |  | FALSE
DP_CLR21 | 52C1 TCM TRIP1 | [5 empty] | FALSE |  | FALSE
DP_ELE22 | IN211 | 52C1 TCM Trip 2 | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET22 | [6 empty] | FALSE |  | FALSE
DP_CLR22 | 52C1 TCM TRIP2 | [5 empty] | FALSE |  | FALSE
DP_ELE23 | IN212 | 52C1 in Local | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET23 | 52C1 IN LCL | [5 empty] | FALSE |  | FALSE
DP_CLR23 | [6 empty] | FALSE |  | FALSE
DP_ELE24 | IN213 | CSW1 DC Close Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET24 | [6 empty] | FALSE |  | FALSE
DP_CLR24 | CSW1 74DC CLOSE | [5 empty] | FALSE |  | FALSE
DP_ELE25 | IN214 | CSW1 DC Trip Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET25 | [6 empty] | FALSE |  | FALSE
DP_CLR25 | CSW1 74DC TRIP | [5 empty] | FALSE |  | FALSE
DP_ELE26 | IN215 | CSW1 Lockout Trip | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET26 | 86CSW1 LCKOUT | [5 empty] | FALSE |  | FALSE
DP_CLR26 | [6 empty] | FALSE |  | FALSE
DP_ELE27 | IN218 | CSW1 Loss of AC | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET27 | CSW1 27AC | [5 empty] | FALSE |  | FALSE
DP_CLR27 | [6 empty] | FALSE |  | FALSE
DP_ELE28 | IN219 | CSW1 Loss of DC | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET28 | CSW1 27DC | [5 empty] | FALSE |  | FALSE
DP_CLR28 | [6 empty] | FALSE |  | FALSE
DP_ELE29 | IN222 | CSW1 Spring Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET29 | CSW1 SPRNG ALM | [5 empty] | FALSE |  | FALSE
DP_CLR29 | [6 empty] | FALSE |  | FALSE
DP_ELE30 | IN220 | CSW1 SF6 Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET30 | CSW1 SF6 ALM | [5 empty] | FALSE |  | FALSE
DP_CLR30 | [6 empty] | FALSE |  | FALSE
DP_ELE31 | IN221 | CSW1 SF6 Lockout | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET31 | CSW1 SF6 LCKOUT | [5 empty] | FALSE |  | FALSE
DP_CLR31 | [6 empty] | FALSE |  | FALSE
DP_ELE32 | IN223 | CSW1 in Local | Display Points | Alarm |  |  | FALSE |  | FALSE
DP_SET32 | CSW1 IN LCL | [5 empty] | FALSE |  | FALSE
DP_CLR32 | [6 empty] | FALSE |  | FALSE
DP_ELE33 | IN301 | CSW2 DC Close Alarm | Display Points | Alarm |  | 2,3 | FALSE |  | FALSE
DP_SET33 | [5 empty] | 2,3 | FALSE |  | FALSE
DP_CLR33 | CSW2 74DC CLOSE |  |  |  |  | 2,3 | FALSE |  | FALSE
DP_ELE34 | IN302 | CSW2 DC Trip Alarm | Display Points | Alarm |  | 2,3 | FALSE |  | FALSE
DP_SET34 | [5 empty] | 2,3 | FALSE |  | FALSE
DP_CLR34 | CSW2 74DC TRIP |  |  |  |  | 2,3 | FALSE |  | FALSE
DP_ELE35 | IN303 | CSW2 Lockout Trip | Display Points | Alarm |  | 2,3 | FALSE |  | FALSE
DP_SET35 | 86CSW2 LCKOUT |  |  |  |  | 2,3 | FALSE |  | FALSE
DP_CLR35 | [5 empty] | 2,3 | FALSE |  | FALSE
DP_ELE36 | IN306 | CSW2 Loss of AC | Display Points | Inactive |  | 2,3 | FALSE |  | FALSE
DP_SET36 | CSW2 27AC |  |  |  |  | 2,3 | FALSE |  | FALSE
DP_CLR36 | [5 empty] | 2,3 | FALSE |  | FALSE
DP_ELE37 | IN307 | CSW2 Loss of DC | Display Points | Alarm |  | 2,3 | FALSE |  | FALSE
DP_SET37 | CSW2 27DC |  |  |  |  | 2,3 | FALSE |  | FALSE
DP_CLR37 | [5 empty] | 2,3 | FALSE |  | FALSE
DP_ELE38 | IN310 | CSW2 Spring Alarm | Display Points | Alarm |  | 2,3 | FALSE |  | FALSE
DP_SET38 | CSW2 SPRNG ALM |  |  |  |  | 2,3 | FALSE |  | FALSE
DP_CLR38 | [5 empty] | 2,3 | FALSE |  | FALSE
DP_ELE39 | IN308 | CSW2 SF6 Alarm | Display Points | Alarm |  | 2,3 | FALSE |  | FALSE
DP_SET39 | CSW2 SF6 ALM |  |  |  |  | 2,3 | FALSE |  | FALSE
DP_CLR39 | [5 empty] | 2,3 | FALSE |  | FALSE
DP_ELE40 | IN309 | CSW2 SF6 Lockout | Display Points | Alarm |  | 2,3 | FALSE |  | FALSE
DP_SET40 | CSW2 SF6 LCKOUT |  |  |  |  | 2,3 | FALSE |  | FALSE
DP_CLR40 | [5 empty] | 2,3 | FALSE |  | FALSE
DP_ELE41 | IN311 | CSW2 in Local | Display Points | Alarm |  | 2,3 | FALSE |  | FALSE
DP_SET41 | CSW2 IN LCL |  |  |  |  | 2,3 | FALSE |  | FALSE
DP_CLR41 | [5 empty] | 2,3 | FALSE |  | FALSE
DP_ELE42 | [6 empty] | FALSE |  | FALSE
DP_SET42 | [6 empty] | FALSE |  | FALSE
DP_CLR42 | [6 empty] | FALSE |  | FALSE
PB1_LED | PLT01 | 52C1 Remote Enable | LED | Indication |  |  | FALSE |  | TRUE
PB1_COL | GO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
PB2_LED | PLT02 | Undervoltage Disable | LED | Indication |  |  | FALSE |  | TRUE
PB2_COL | RO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
PB3_LED | PLT03 | Breaker Failure Disable | LED | Indication |  |  | FALSE |  | TRUE
PB3_COL | RO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
PB4_LED | PLT04 | Breaker Failed (push to reset) | LED | Indication |  |  | FALSE |  | TRUE
PB4_COL | RO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
PB5_LED | PLT05 | Trip Coil Failed (push to reset) | LED | Indication |  |  | FALSE |  | TRUE
PB5_COL | RO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
PB6_LED | NOT PLT06 | Operator Lock (hold to disable) | LED | Indication |  |  | FALSE |  | TRUE
PB6_COL | GO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
PB7_LED | PLT07 OR PLT08 OR PLT09 | CAP Unbalance (push to reset) | LED | Indication |  |  | FALSE |  | TRUE
PB7_COL | RO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
PB8_LED | PLT10 | Auto Control Enable | LED | Indication |  |  | FALSE |  | TRUE
PB8_COL | GO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
PB9_LED | PLT11 | CSW1 Auto/Remote Enable | LED | Indication |  |  | FALSE |  | TRUE
PB9_COL | GO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
PB10LED | PLT12 | CSW2 Auto/Remote Enable | LED | Indication |  | 2,3 | FALSE |  | TRUE
PB10COL | GO | LED Color | LED | Indication |  | 2,3 | FALSE |  | FALSE
PB11LED | PLT13 | CSW3 Auto/Remote Enable | LED | Indication |  | 3 | FALSE |  | TRUE
PB11COL | GO | LED Color | LED | Indication |  | 3 | FALSE |  | FALSE
PB12LED | 0 | Not Used | LED | Indication |  |  | FALSE |  | TRUE
PB12COL | GO | LED Color | LED | Indication |  |  | FALSE |  | FALSE
T1_LED | 87TG1D OR 87HG1D | CAP1 Unbalance Trip | LED | Indication |  |  | FALSE |  | FALSE
T1EDL | Y | CAP1 Unbalance Trip | LED | Indication |  |  | FALSE |  | FALSE
T1EDC | RO | CAP1 Unbalance Trip | LED | Indication |  |  | FALSE |  | FALSE
T2_LED | 0 | Not Used | LED | Indication |  | 1 | FALSE |  | FALSE
T2_LED | 87TG2D OR 87HG2D | CAP2 Unbalance Trip | LED | Indication |  | 2,3 | FALSE |  | FALSE
T2EDL | Y | CAP2 Unbalance Trip | LED | Indication |  | 2,3 | FALSE |  | FALSE
T2EDC | RO | CAP2 Unbalance Trip | LED | Indication |  | 2,3 | FALSE |  | FALSE
T3_LED | 0 | Not Used | LED | Indication |  | 1,2 | FALSE |  | FALSE
T3_LED | 87TG3D OR 87HG3D | CAP3 Unbalance Trip | LED | Indication |  | 3 | FALSE |  | FALSE
T3EDL | Y | CAP3 Unbalance Trip | LED | Indication |  | 3 | FALSE |  | FALSE
T3EDC | RO | CAP3 Unbalance Trip | LED | Indication |  | 3 | FALSE |  | FALSE
T4_LED | 50WP1 OR 50WG1 | Instantaneous Trip | LED | Indication |  |  | FALSE |  | FALSE
T4EDL | Y | Instantaneous Trip | LED | Indication |  |  | FALSE |  | FALSE
T4EDC | RO | Instantaneous Trip | LED | Indication |  |  | FALSE |  | FALSE
T5_LED | 51S01 OR 51S02 OR 51S03 | Time Overcurrent Pickup | LED | Indication |  |  | FALSE |  | FALSE
T5EDL | Y | Time Overcurrent Pickup | LED | Indication |  |  | FALSE |  | FALSE
T5EDC | RO | Time Overcurrent Pickup | LED | Indication |  |  | FALSE |  | FALSE
T6_LED | 51T01 OR 51T02 OR 51T03 | Time Overcurrent Trip | LED | Indication |  |  | FALSE |  | FALSE
T6EDL | Y | Time Overcurrent Trip | LED | Indication |  |  | FALSE |  | FALSE
T6EDC | RO | Time Overcurrent Trip | LED | Indication |  |  | FALSE |  | FALSE
T7_LED | 50WG1 OR 51T02 | Ground Fault | LED | Indication |  |  | FALSE |  | FALSE
T7EDL | Y | Ground Fault | LED | Indication |  |  | FALSE |  | FALSE
T7EDC | RO | Ground Fault | LED | Indication |  |  | FALSE |  | FALSE
T8_LED | 271P1T AND NOT PLT02 | Undervoltage Trip | LED | Indication |  |  | FALSE |  | FALSE
T8EDL | Y | Undervoltage Trip | LED | Indication |  |  | FALSE |  | FALSE
T8EDC | RO | Undervoltage Trip | LED | Indication |  |  | FALSE |  | FALSE
T9_LED | 591P1T | Overvoltage Trip | LED | Indication |  |  | FALSE |  | FALSE
T9EDL | Y | Overvoltage Trip | LED | Indication |  |  | FALSE |  | FALSE
T9EDC | RO | Overvoltage Trip | LED | Indication |  |  | FALSE |  | FALSE
T10_LED | PCT12Q | CAP1 Discharging | LED | Indication |  |  | FALSE |  | FALSE
T10EDL | Y | CAP1 Discharging | LED | Indication |  |  | FALSE |  | FALSE
T10EDC | RO | CAP1 Discharging | LED | Indication |  |  | FALSE |  | FALSE
T11_LED | 0 | Not Used | LED | Indication |  | 1 | FALSE |  | FALSE
T11_LED | PCT13Q | CAP2 Discharging | LED | Indication |  | 2,3 | FALSE |  | FALSE
T11EDL | Y | CAP2 Discharging | LED | Indication |  | 2,3 | FALSE |  | FALSE
T11EDC | RO | CAP2 Discharging | LED | Indication |  | 2,3 | FALSE |  | FALSE
T12_LED | 0 | Not Used | LED | Indication |  | 1,2 | FALSE |  | FALSE
T12_LED | PCT14Q | CAP3 Discharging | LED | Indication |  | 3 | FALSE |  | FALSE
T12EDL | Y | CAP3 Discharging | LED | Indication |  | 3 | FALSE |  | FALSE
T12EDC | RO | CAP3 Discharging | LED | Indication |  | 3 | FALSE |  | FALSE
T13_LED | ASV110 | CAP1 Available | LED | Indication |  |  | FALSE |  | FALSE
T13EDL | Y | CAP1 Available | LED | Indication |  |  | FALSE |  | FALSE
T13EDC | RO | CAP1 Available | LED | Indication |  |  | FALSE |  | FALSE
T14_LED | 0 | Not Used | LED | Indication |  | 1 | FALSE |  | FALSE
T14_LED | ASV111 | CAP2 Available | LED | Indication |  | 2,3 | FALSE |  | FALSE
T14EDL | Y | CAP2 Available | LED | Indication |  | 2,3 | FALSE |  | FALSE
T14EDC | RO | CAP2 Available | LED | Indication |  | 2,3 | FALSE |  | FALSE
T15_LED | 0 | Not Used | LED | Indication |  | 1,2 | FALSE |  | FALSE
T15_LED | ASV112 | CAP3 Available | LED | Indication |  | 3 | FALSE |  | FALSE
T15EDL | Y | CAP3 Available | LED | Indication |  | 3 | FALSE |  | FALSE
T15EDC | RO | CAP3 Available | LED | Indication |  | 3 | FALSE |  | FALSE
T16_LED | TIRIG | IRIG OK | LED | Indication |  |  | FALSE |  | FALSE
T16EDL | Y | IRIG OK | LED | Indication |  |  | FALSE |  | FALSE
T16EDC | GO | IRIG OK | LED | Indication |  |  | FALSE |  | FALSE
T17_LED | PCT26Q | SCADA Operation | LED | Indication |  |  | FALSE |  | FALSE
T17EDL | Y | SCADA Operation | LED | Indication |  |  | FALSE |  | FALSE
T17EDC | RO | SCADA Operation | LED | Indication |  |  | FALSE |  | FALSE
T18_LED | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T18EDL | Y | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T18EDC | RO | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T19_LED | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T19EDL | Y | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T19EDC | RO | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T20_LED | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T20EDL | Y | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T20EDC | RO | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T21_LED | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T21EDL | Y | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T21EDC | RO | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T22_LED | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T22EDL | Y | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T22EDC | RO | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T23_LED | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T23EDL | Y | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T23EDC | RO | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T24_LED | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T24EDL | Y | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T24EDC | RO | Not Used | LED | Indication |  |  | FALSE |  | FALSE
SITM1 | IN101 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM2 | IN102 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM3 | IN103 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM4 | IN104 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM5 | IN105 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM6 | IN106 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM7 | IN107 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM8 | OUT101 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM9 | OUT102 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM10 | OUT103 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM11 | OUT104 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM12 | OUT105 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM13 | OUT106 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM14 | OUT107 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM15 | OUT108 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM16 | IN201 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM17 | IN202 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM18 | IN203 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM19 | IN204 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM20 | IN205 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM21 | IN206 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM22 | IN207 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM23 | IN208 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM24 | IN209 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM25 | IN210 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM26 | IN211 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM27 | IN212 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM28 | IN213 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM29 | IN214 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM30 | IN215 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM31 | IN216 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM32 | IN217 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM33 | IN218 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM34 | IN219 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM35 | IN220 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM36 | IN221 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM37 | IN222 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM38 | IN223 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM39 | IN224 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM40 | OUT201 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM41 | OUT202 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM42 | OUT203 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM43 | OUT204 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM44 | IN301 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM45 | IN302 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM46 | IN303 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM47 | IN304 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM48 | IN305 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM49 | IN306 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM50 | IN307 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM51 | IN308 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM52 | IN309 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM53 | IN310 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM54 | IN311 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM55 | IN312 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM56 | IN313 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM57 | IN314 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM58 | IN315 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM59 | IN316 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM60 | IN317 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM61 | IN318 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM62 | IN319 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM63 | IN320 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM64 | IN321 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM65 | IN322 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM66 | IN323 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM67 | IN324 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM68 | OUT301 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM69 | OUT302 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM70 | OUT303 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM71 | OUT304 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM72 | OUT305 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM73 | OUT306 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM74 | OUT307 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM75 | OUT308 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM76 | TRW | SER | Report | SER |  |  | FALSE |  | FALSE
SITM77 | 50WP1 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM78 | 50WG1 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM79 | 51T01 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM80 | 51T02 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM81 | 271P1T | SER | Report | SER |  |  | FALSE |  | FALSE
SITM82 | 591P1T | SER | Report | SER |  |  | FALSE |  | FALSE
SITM83 | 87AG1D | SER | Report | SER |  |  | FALSE |  | FALSE
SITM84 | 87TG1D | SER | Report | SER |  |  | FALSE |  | FALSE
SITM85 | 87HG1D | SER | Report | SER |  |  | FALSE |  | FALSE
SITM86 | 87AG2D | SER | Report | SER |  |  | FALSE |  | FALSE
SITM87 | 87TG2D | SER | Report | SER |  |  | FALSE |  | FALSE
SITM88 | 87HG2D | SER | Report | SER |  |  | FALSE |  | FALSE
SITM89 | 87AG3D | SER | Report | SER |  |  | FALSE |  | FALSE
SITM90 | 87TG3D | SER | Report | SER |  |  | FALSE |  | FALSE
SITM91 | 87HG3D | SER | Report | SER |  |  | FALSE |  | FALSE
SITM92 | PSV01 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM93 | PSV02 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM94 | PSV03 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM95 | PSV04 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM96 | PSV05 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM97 | PSV06 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM98 | PSV07 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM99 | PSV08 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM100 | PSV09 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM101 | PSV10 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM102 | PSV11 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM103 | PSV12 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM104 | PSV13 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM105 | PCT01Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM106 | PCT02Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM107 | PCT03Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM108 | PCT04Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM109 | PCT05Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM110 | PCT06Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM111 | PCT07Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM112 | PCT08Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM113 | PCT09Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM114 | PCT10Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM115 | PCT11Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM116 | PCT12Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM117 | PCT13Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM118 | PCT14Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM119 | PCT15Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM120 | PCT16Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM121 | PCT17Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM122 | PCT18Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM123 | PCT19Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM124 | PCT20Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM125 | PCT21Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM126 | PCT22Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM127 | PCT23Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM128 | PCT24Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM129 | PCT25Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM130 | PCT26Q | SER | Report | SER |  |  | FALSE |  | FALSE
SITM131 | PLT01 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM132 | PLT02 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM133 | PLT03 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM134 | PLT04 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM135 | PLT05 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM136 | PLT06 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM137 | PLT07 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM138 | PLT08 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM139 | PLT09 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM140 | PLT10 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM141 | PLT11 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM142 | PLT12 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM143 | PLT13 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM144 | RB01 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM145 | RB02 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM146 | RB03 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM147 | RB04 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM148 | RB05 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM149 | RB06 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM150 | RB07 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM151 | RB08 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM152 | RB09 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM153 | RB10 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM154 | RB11 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM155 | RB12 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM156 | RB13 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM157 | RB14 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM158 | RB15 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM159 | PB1 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM160 | PB2 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM161 | PB3 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM162 | PB4 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM163 | PB5 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM164 | PB6 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM165 | PB7 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM166 | PB8 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM167 | PB9 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM168 | PB10 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM169 | PB11 | SER | Report | SER |  |  | FALSE |  | FALSE
SITM170 | PB12 | SER | Report | SER |  |  | FALSE |  | FALSE
ERDG1 | IN101 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG2 | IN102 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG3 | IN103 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG4 | IN104 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG5 | IN105 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG6 | IN106 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG7 | IN107 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG8 | OUT101 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG9 | OUT102 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG10 | OUT103 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG11 | OUT104 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG12 | OUT105 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG13 | OUT106 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG14 | OUT107 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG15 | OUT108 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG16 | IN201 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG17 | IN202 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG18 | IN203 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG19 | IN204 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG20 | IN205 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG21 | IN206 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG22 | IN207 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG23 | IN208 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG24 | IN209 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG25 | IN210 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG26 | IN211 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG27 | IN212 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG28 | IN213 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG29 | IN214 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG30 | IN215 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG31 | IN216 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG32 | IN217 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG33 | IN218 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG34 | IN219 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG35 | IN220 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG36 | IN221 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG37 | IN222 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG38 | IN223 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG39 | IN224 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG40 | OUT201 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG41 | OUT202 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG42 | OUT203 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG43 | OUT204 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG44 | IN301 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG45 | IN302 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG46 | IN303 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG47 | IN304 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG48 | IN305 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG49 | IN306 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG50 | IN307 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG51 | IN308 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG52 | IN309 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG53 | IN310 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG54 | IN311 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG55 | IN312 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG56 | IN313 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG57 | IN314 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG58 | IN315 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG59 | IN316 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG60 | IN317 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG61 | IN318 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG62 | IN319 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG63 | IN320 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG64 | IN321 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG65 | IN322 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG66 | IN323 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG67 | IN324 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG68 | OUT301 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG69 | OUT302 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG70 | OUT303 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG71 | OUT304 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG72 | OUT305 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG73 | OUT306 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG74 | OUT307 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG75 | OUT308 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG76 | TRW | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG77 | 50WP1T | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG78 | 50WP1 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG79 | 50WG1T | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG80 | 50WG1 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG81 | 51T01 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG82 | 51S01 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG83 | 51T02 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG84 | 51S02 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG85 | 271P1T | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG86 | 271P1 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG87 | 591P1T | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG88 | 591P1 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG89 | 87AG1D | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG90 | 87AG1 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG91 | 87TG1D | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG92 | 87TG1 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG93 | 87HG1D | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG94 | 87HG1 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG95 | 87AG2D | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG96 | 87AG2 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG97 | 87TG2D | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG98 | 87TG2 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG99 | 87HG2D | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG100 | 87HG2 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG101 | 87AG3D | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG102 | 87AG3 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG103 | 87TG3D | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG104 | 87TG3 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG105 | 87HG3D | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG106 | 87HG3 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG107 | PSV01 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG108 | PSV02 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG109 | PSV03 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG110 | PSV04 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG111 | PSV05 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG112 | PSV06 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG113 | PSV07 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG114 | PSV08 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG115 | PSV09 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG116 | PSV10 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG117 | PSV11 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG118 | PSV12 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG119 | PSV13 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG120 | PCT01Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG121 | PCT02Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG122 | PCT03Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG123 | PCT04Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG124 | PCT05Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG125 | PCT06Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG126 | PCT07Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG127 | PCT08Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG128 | PCT09Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG129 | PCT10Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG130 | PCT11Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG131 | PCT12Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG132 | PCT13Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG133 | PCT14Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG134 | PCT15Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG135 | PCT16Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG136 | PCT17Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG137 | PCT18Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG138 | PCT19Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG139 | PCT20Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG140 | PCT21Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG141 | PCT22Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG142 | PCT23Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG143 | PCT24Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG144 | PCT25Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG145 | PCT26Q | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG146 | PLT01 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG147 | PLT02 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG148 | PLT03 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG149 | PLT04 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG150 | PLT05 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG151 | PLT06 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG152 | PLT07 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG153 | PLT08 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG154 | PLT09 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG155 | PLT10 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG156 | PLT11 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG157 | PLT12 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG158 | PLT13 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG159 | RB01 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG160 | RB02 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG161 | RB03 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG162 | RB04 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG163 | RB05 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG164 | RB06 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG165 | RB07 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG166 | RB08 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG167 | RB09 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG168 | RB10 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG169 | RB11 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG170 | RB12 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG171 | RB13 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG172 | RB14 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERDG173 | RB15 | Event Report Digital | Report | Event |  |  | FALSE |  | FALSE
ERAQ1 | IAWFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ2 | IAWFAC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ3 | IBWFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ4 | IBWFAC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ5 | ICWFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ6 | ICWFAC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ7 | VAYFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ8 | VAYFAC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ9 | VBYFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ10 | VBYFAC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ11 | VCYFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ12 | VCYFAC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ13 | VAZFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ14 | VBZFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ15 | VCZFMC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ16 | 3PWFC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ17 | 3QWFC | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ18 |  | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ19 |  | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ20 |  | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
EPORT | Y | Enable Port F | Communications | Port F |  |  | FALSE | PF | FALSE
PROTO | SEL | Protocol | Communications | Port F |  |  | FALSE | PF | FALSE
MAXACC | C | Max Access Level | Communications | Port F |  |  | FALSE | PF | FALSE
SPEED | 19200 | Baud Rate | Communications | Port F |  |  | FALSE | PF | FALSE
DATABIT | 8 | Data Bits | Communications | Port F |  |  | FALSE | PF | FALSE
PARITY | N | Parity | Communications | Port F |  |  | FALSE | PF | FALSE
STOPBIT | 1 | Stop Bits | Communications | Port F |  |  | FALSE | PF | FALSE
FASTOP | Y | Fast Operate Enable | Communications | Port F |  |  | FALSE | PF | FALSE
EPORT | N | Enable Port 1 | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EPORT | N | Enable Port 2 | Communications | Port 2 |  |  | FALSE | P2 | FALSE
EPORT | N | Enable Port 3 | Communications | Port 3 |  |  | FALSE | P3 | FALSE
EPORT | Y | Enable Port 5 | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DEFRTR | 172.31.100.254 | Default Router | Communications | Port 5 |  |  | FALSE | P5 | FALSE
NETMODE | FAILOVER | Operating Mode | Communications | Port 5 |  |  | FALSE | P5 | FALSE
NETPORT | C | Primary Network Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ETELNET | Y | Enable Telnet | Communications | Port 5 |  |  | FALSE | P5 | FALSE
TPORT | 23 | Telnet Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
FASTOP | Y | Fast Operate Enable | Communications | Port 5 |  |  | FALSE | P5 | FALSE
EDNP | 2 | Enable DNP Sessions | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPNUM | 20000 | DNP Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPADR | 1 | DNP Server Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPIP1 | 172.31.100.241 | DNP Client IP Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPTR1 | TCP | DNP Transport Protocol | Communications | Port 5 |  |  | FALSE | P5 | FALSE
REPADR1 | 0 | DNP Client Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPMAP1 | 1 | DNP Session Map | Communications | Port 5 |  |  | FALSE | P5 | FALSE
AIVAR1 | 5 | AI Default Variation | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLA1 | 0 | Current Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLV1 | 0 | Volt Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLM1 | 0 | Misc Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBA1 | 0 | Amps Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBV1 | 0 | Volts Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBM1 | 0 | Misc Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPIP2 | 172.31.100.243 | DNP Client IP Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPTR2 | TCP | DNP Transport Protocol | Communications | Port 5 |  |  | FALSE | P5 | FALSE
REPADR2 | 0 | DNP Client Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPMAP2 | 1 | DNP Session Map | Communications | Port 5 |  |  | FALSE | P5 | FALSE
AIVAR2 | 5 | AI Default Variation | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLA2 | 0 | Current Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLV2 | 0 | Volt Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLM2 | 0 | Misc Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBA2 | 0 | Amps Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBV2 | 0 | Volts Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBM2 | 0 | Misc Reporting Deadband | Communications | Port 5 |  |  | FALSE | P5 | FALSE
EPMIP | N | Enable PMU Comms | Communications | Port 5 |  |  | FALSE | P5 | FALSE
PMOTS1 | TCP | PMU Output1 Transport Scheme | Communications | Port 5 |  |  | FALSE | P5 | FALSE
PMOIPA1 | 172.31.100.38 | PMU Output1 Client IP | Communications | Port 5 |  |  | FALSE | P5 | FALSE
BI_1 | EN_RLY | Relay Enabled | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_2 | TRIPLED | Trip | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_3 | PB1_LED | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_4 | PB2_LED | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_5 | PB3_LED | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_6 | PB4_LED | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_7 | PB5_LED | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_8 | PB6_LED | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_9 | PB7_LED | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_10 | PB8_LED | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_11 | PB9_LED | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_12 | PB10LED | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_13 | TLED_1 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_14 | TLED_2 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_15 | TLED_3 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_16 | TLED_4 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_17 | TLED_5 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_18 | TLED_6 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_19 | TLED_7 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_20 | TLED_8 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_21 | TLED_9 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_22 | TLED_10 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_23 | TLED_11 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_24 | TLED_12 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_25 | TLED_13 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_26 | TLED_14 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_27 | TLED_15 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_28 | TLED_16 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_29 | TLED_17 | LED | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_30 | IN101 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_31 | IN102 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_32 | OUT105 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_33 | IN201 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_34 | IN202 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_35 | IN203 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_36 | IN204 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_37 | IN205 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_38 | IN206 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_39 | IN207 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_40 | IN208 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_41 | IN209 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_42 | IN210 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_43 | IN211 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_44 | IN212 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_45 | IN213 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_46 | IN214 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_47 | IN215 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_48 | IN216 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_49 | IN217 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_50 | IN218 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_51 | IN219 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_52 | IN220 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_53 | IN221 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_54 | IN222 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_55 | IN223 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_56 | IN224 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_57 | OUT204 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_58 | IN301 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_59 | IN302 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_60 | IN303 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_61 | IN304 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_62 | IN305 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_63 | IN306 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_64 | IN307 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_65 | IN308 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_66 | IN309 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_67 | IN310 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_68 | IN311 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_69 | IN312 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_70 | OUT304 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_71 | IN103 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_72 | IN104 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_73 | PCT05Q | TCM Alarms | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_74 | PCT06Q | TCM Alarms | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_75 | PCT07Q | TCM Alarms | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_76 | PCT08Q | TCM Alarms | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_77 | PCT02Q | TCM Alarms | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_78 | PCT03Q | TCM Alarms | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_1 | IAWFMC | Current A | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_2 | IBWFMC | Current B | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_3 | ICWFMC | Current C | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_4 | VAYFMC | Bus Voltage A | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_5 | VBYFMC | Bus Voltage B | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_6 | VCYFMC | Bus Voltage C | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_7 | VABYFMC | Bus Voltage AB | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_8 | VBCYFMC | Bus Voltage BC | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_9 | VCAYFMC | Bus Voltage CA | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_10 | AMV004 | CAPA Neutral Voltage | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_11 | AMV005 | CAPB Neutral Voltage | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_12 | AMV006 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_13 | 3PWFC | Real Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_14 | 3QWFC | Reactive Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_15 | FREQ | Frequency | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_16 | VDC | Battery Voltage | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_17 | AMV001 | CSW1 Op Counter | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_18 | AMV002 | CSW2 Op Counter | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_19 | AMV003 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_1 | RB01 | 52C1 Remote Open | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_2 | RB02 | 52C1 Remote Close | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_3 | RB03 | CSW1 Auto Open | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_4 | RB04 | CSW1 Auto Close | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_5 | RB05 | CSW1 Remote Open | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_6 | RB06 | CSW1 Remote Close | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_7 | RB07 | CSW2 Auto Open | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_8 | RB08 | CSW2 Auto Close | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_9 | RB09 | CSW2 Remote Open | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_10 | RB10 | CSW2 Remote Close | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_11 | RB11 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_12 | RB12 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_13 | RB13 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_14 | RB14 | Not Used | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_15 | RB15 | Target Reset | Communications | DNP 1 |  |  | FALSE | D1 | FALSE

## BUS_587Z
SEL-587Z Bus Protection Settings & Logic
Relay Specification
Manufacturer | SEL
Model | SEL-587Z
Part # | 0587Z0X325H12XX
Function | Bus Protection
Front View |  |  |  | Rear View
Relay Classification
Relay ID (RID) | Setpoint Class | Logic Class
87B | A | 1
I/O Summary
I/O | Description
IN1 | 86B Trip Coil Monitor
IN2 | 86B Status
OUT1 | 86B Lockout Trip
OUT2 | Spare
OUT3 | Not Used
OUT4 | 87B Fault Indicator
ALARM | Relay Fail Alarm
Ratios |  | Setpoint Class
| Element | A | B | C | D | E
| CTR | 600
Short Circuit Current Values
Relay | Setpoint Class | Fault Location | 3 PH (A-pri) | SLG (A-pri)
87B | A | 34.5kV MV1 | 30123 | 17777
87B2 | B | 34.5kV MV2 | 18763 | 14019
87B3 | C | 34.5kV MV3 | 30865 | 17850
Diff Voltage Pickup Calculations
Relay | Fault Type | N | Rct | Lead Length | Rlead | If | P | Vr | Vs
87B | 3Θ | 800 | 1.19 | 510 | 0.612 | 30123 | 1 | 67.8521 | 84.8151
87B | SLG | 800 | 1.19 | 510 | 0.612 | 17777 | 2 | 53.6421 | 67.0526
87B2 | 3Θ | 600 | 0.79 | 913 | 1.096 | 18763 | 1 | 58.9784 | 73.723
87B2 | SLG | 600 | 0.79 | 913 | 1.096 | 14019 | 2 | 69.6744 | 87.093
87B3 | 3Θ | 800 | 1.19 | 1052 | 1.262 | 30865 | 1 | 94.6012 | 118.2515
87B3 | SLG | 800 | 1.19 | 1052 | 1.262 | 17850 | 2 | 82.8686 | 103.5858
Diff Voltage Calc Philosophy
N = CT ratio Rct = max CT internal resistance Rlead = max CT lead resistance Resistance of #10 AWG = 1.2Ω/1000ft If = Maximum external fault current (max fault at feeders) P = Lead length factor = 1 for three phase faults ¦ 2 for single phase faults Vr = Voltage across high-impedance differential element Vr = (If/N)∗(Rct +P∗Rlead)
87B Differential Settings |  | Setpoint Class
Level 1 |  | A | B | C | D | E
Pickup, A Phase | 87A1P (V-sec) | 200
Pickup, B Phase | 87B1P (V-sec) | 200
Pickup, C Phase | 87C1P (V-sec) | 200
Delay | SV5PU (cyc) | 1.125
Level 2 (Open CT Detector) |  | A | B | C | D | E
Pickup, A Phase | 87A2P (V-sec) | 20
Pickup, B Phase | 87B2P (V-sec) | 20
Pickup, C Phase | 87C2P (V-sec) | 20
Delay | SV8DO (cyc) | 1.125
87B Differential Philosophy
Level 1 will be used for tripping. 200 V is the minimum setting recommended by the manufacturer. The voltage differential pickup threshold (Vs) is proportional to Vr. A safety factor of 1.25 will be used. Select the highest voltage differential pickup threshold associated with each relay for the Level 1 pickup. If the calculated threshold is below the minimum, use the minimum setting. Vs < 200 V Set 87x1P = 200 V Surge arresters in the differential zone necessitate delayed tripping. Delay = arrester conducting time + 0.75 cycle filter decay + 0.25 cycle margin Assumed arrester conducting time = 0.125 cycles Delay = 1.125 cycles Level 2 is used for open CT detection alarming. 87x2P = min pickup = 20 V Surge arresters in the differential zone necessitate delayed tripping. Delay = arrester conducting time + 0.75 cycle filter decay + 0.25 cycle margin Assumed arrester conducting time = 0.125 cycles Delay = 1.125 cycles
Minimum Operating Current Calculations
Relay | n | Ie (mA) | Ir (mA) | Im | N | Imin (A)
87HBA/B | 4 | 30 | 100 | 0 | 600 | 132
87B | 12 | 8 | 100 | 0 | 800 | 156.8
87B2 | 6 | 9 | 100 | 0 | 600 | 92.4
87B3 | 13 | 8 | 100 | 0 | 800 | 163.2
Minimum Operating Current Calculations Philosophy
The minimum primary current required to operate the differential elements is used to gauge the sensitivity of the bus protection and provides the following application-specific information: Provides an indication of the load current below which the open CT detection logic will work. Above this load current, the relay will trip for an open CT. Defines the peak load current that a tapped load such as an auxiliary transformer can draw inside the bus differential zone. Defines the maximum primary current that will not cause a bus differential relay operation for a secondary fault on an auxiliary transformer or PT connection inside the bus differential zone. Imin = (n*Ie + Ir + Im)*N Imin = minimum current n = number of current transformers in parallel with the relay, per phase Ie = current transformer exciting current at relay setting voltage (Vs) Assume 10 mA if curve unavailable Ir = current through the relay at relay setting voltage (Vs) Ir = Vs/2000 Im = current through the MOV at relay setting voltage (Vs) ~0 for applications with Vs below 1000 V
PH OC Settings |  | Setpoint Class
Level 1 |  | A | B | C | D | E
Pickup, A Phase | 50A1P (A-sec) | 2.5
Pickup, B Phase | 50B1P (A-sec) | 2.5
Pickup, C Phase | 50C1P (A-sec) | 2.5
Delay | SV7PU (cyc) | 1.625
Level 2 (Current Detector) |  | A | B | C | D | E
FLA | A-pri | 441.632
Pickup, A Phase | 50A2P (A-sec) | 0.7
Pickup, B Phase | 50B2P (A-sec) | 0.7
Pickup, C Phase | 50C2P (A-sec) | 0.7
Delay | SV8DO (cyc) | 3600
OC Elements Philosophy
Level 1 serves as an MOV degradation and backup protection element. The pickup and delay are set per manufacturer recommendation considering the presence of surge arrestors within the zone of protection. 50x1P (SV7) = 2.5 A Delay = arrestor conducting time + cycle filter decay + margin Delay = 0.125 + 1.25 + 0.25 = 1.625 cycles Level 2 serves as a current detector for MOV failure and will be set to the full load amps of the main power transformer. 50x2P (SV8) = FLA/CT ratio Dropout Delay = 3600 cycles
Settings Table
Setting | Value | Description | Category | Function | Setpoint Class | Logic Class | Float | QuickSet Group | SER
TID | GRVR HL WND | Terminal Identifier | Device | General |  |  | FALSE |  | FALSE
NFREQ | 60 | Nominal Frequency (Hz) | Device | General |  |  | FALSE |  | FALSE
PHROT | ABC | Phase Rotation | Device | General |  |  | FALSE |  | FALSE
CTR | 600 | Phase CT Ratio (IA, IB, IC) | Device | Ratio | A |  | FALSE |  | FALSE
CTR | 0 | Phase CT Ratio (IA, IB, IC) | Device | Ratio | B |  | FALSE |  | FALSE
CTR | 0 | Phase CT Ratio (IA, IB, IC) | Device | Ratio | C |  | FALSE |  | FALSE
87A1P | 200 | Level 1 87B Pickup (V-sec) | Protection Setpoints | Differential | A |  | FALSE |  | FALSE
87A1P | 0 | Level 1 87B Pickup (V-sec) | Protection Setpoints | Differential | B |  | FALSE |  | FALSE
87A1P | 0 | Level 1 87B Pickup (V-sec) | Protection Setpoints | Differential | C |  | FALSE |  | FALSE
87B1P | 200 | Level 1 87B Pickup (V-sec) | Protection Setpoints | Differential | A |  | FALSE |  | FALSE
87B1P | 0 | Level 1 87B Pickup (V-sec) | Protection Setpoints | Differential | B |  | FALSE |  | FALSE
87B1P | 0 | Level 1 87B Pickup (V-sec) | Protection Setpoints | Differential | C |  | FALSE |  | FALSE
87C1P | 200 | Level 1 87B Pickup (V-sec) | Protection Setpoints | Differential | A |  | FALSE |  | FALSE
87C1P | 0 | Level 1 87B Pickup (V-sec) | Protection Setpoints | Differential | B |  | FALSE |  | FALSE
87C1P | 0 | Level 1 87B Pickup (V-sec) | Protection Setpoints | Differential | C |  | FALSE |  | FALSE
87A2P | 20 | Level 2 87B Pickup (V-sec) | Protection Setpoints | Differential | A |  | FALSE |  | FALSE
87A2P | 0 | Level 2 87B Pickup (V-sec) | Protection Setpoints | Differential | B |  | FALSE |  | FALSE
87A2P | 0 | Level 2 87B Pickup (V-sec) | Protection Setpoints | Differential | C |  | FALSE |  | FALSE
87B2P | 20 | Level 2 87B Pickup (V-sec) | Protection Setpoints | Differential | A |  | FALSE |  | FALSE
87B2P | 0 | Level 2 87B Pickup (V-sec) | Protection Setpoints | Differential | B |  | FALSE |  | FALSE
87B2P | 0 | Level 2 87B Pickup (V-sec) | Protection Setpoints | Differential | C |  | FALSE |  | FALSE
87C2P | 20 | Level 2 87B Pickup (V-sec) | Protection Setpoints | Differential | A |  | FALSE |  | FALSE
87C2P | 0 | Level 2 87B Pickup (V-sec) | Protection Setpoints | Differential | B |  | FALSE |  | FALSE
87C2P | 0 | Level 2 87B Pickup (V-sec) | Protection Setpoints | Differential | C |  | FALSE |  | FALSE
50A1P | 2.5 | Level 1 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | A |  | TRUE |  | FALSE
50A1P | 0 | Level 1 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | B |  | TRUE |  | FALSE
50A1P | 0 | Level 1 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | C |  | TRUE |  | FALSE
50B1P | 2.5 | Level 1 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | A |  | TRUE |  | FALSE
50B1P | 0 | Level 1 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | B |  | TRUE |  | FALSE
50B1P | 0 | Level 1 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | C |  | TRUE |  | FALSE
50C1P | 2.5 | Level 1 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | A |  | TRUE |  | FALSE
50C1P | 0 | Level 1 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | B |  | TRUE |  | FALSE
50C1P | 0 | Level 1 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | C |  | TRUE |  | FALSE
50A2P | 0.7 | Level 2 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | A |  | TRUE |  | FALSE
50A2P | 0 | Level 2 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | B |  | TRUE |  | FALSE
50A2P | 0 | Level 2 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | C |  | TRUE |  | FALSE
50B2P | 0.7 | Level 2 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | A |  | TRUE |  | FALSE
50B2P | 0 | Level 2 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | B |  | TRUE |  | FALSE
50B2P | 0 | Level 2 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | C |  | TRUE |  | FALSE
50C2P | 0.7 | Level 2 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | A |  | TRUE |  | FALSE
50C2P | 0 | Level 2 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | B |  | TRUE |  | FALSE
50C2P | 0 | Level 2 PH OC Pickup (A-sec) | Protection Setpoints | Overcurrent | C |  | TRUE |  | FALSE
SV5 | 87A1+87B1+87C1 | Differential Trip | SELogic Variables | Differential |  |  | FALSE |  | FALSE
SV5PU | 1.125 | Differential Trip | SELogic Variables | Differential |  |  | TRUE |  | FALSE
SV5DO | 0 | Differential Trip | SELogic Variables | Differential |  |  | TRUE |  | FALSE
SV6 | 87A2+87B2+87C2 | CT Open Circuit Alarm | SELogic Variables | Alarm |  |  | FALSE |  | FALSE
SV6PU | 18000 | CT Open Circuit Alarm | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV6DO | 0 | CT Open Circuit Alarm | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV7 | 50A1+50B1+50C1 | Backup OC Trip | SELogic Variables | Overcurrent |  |  | FALSE |  | FALSE
SV7PU | 1.625 | Backup OC Trip | SELogic Variables | Overcurrent |  |  | TRUE |  | FALSE
SV7DO | 0 | Backup OC Trip | SELogic Variables | Overcurrent |  |  | TRUE |  | FALSE
SV8 | 50A2+50B2+50C2 | MOV Failure Detector | SELogic Variables | Alarm |  |  | FALSE |  | FALSE
SV8PU | 1 | MOV Failure Detector | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV8DO | 3600 | MOV Failure Detector | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV9 | IN1*!IN2 | Lockout Trip Coil Monitor | SELogic Variables | Alarm |  |  | FALSE |  | FALSE
SV9PU | 30 | Lockout Trip Coil Monitor | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
SV9DO | 0 | Lockout Trip Coil Monitor | SELogic Variables | Alarm |  |  | TRUE |  | FALSE
TR1 | SV5T+SV7T | Trip | Trip Logic | Trip |  |  | FALSE |  | FALSE
ULTR1 | !87A2*!87B2*!87C2*!50A2* !50B2*!50C2 | Unlatch Trip | Trip Logic | Trip |  |  | FALSE |  | FALSE
OUT1 | TRIP1 | 86B Lockout Trip | Outputs | Trip |  |  | FALSE |  | FALSE
DP1 | SV5T | Level 1 Differential Trip | Display Points | Alarm |  |  | FALSE |  | FALSE
DP1_1 | DIFF | Level 1 Differential Trip | Display Points | Alarm |  |  | FALSE |  | FALSE
DP1_0 | NA | Level 1 Differential Trip | Display Points | Alarm |  |  | FALSE |  | FALSE
DP2 | SV6T | Open CT Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP2_1 | OPEN CT | Open CT Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP2_0 | NA | Open CT Alarm | Display Points | Alarm |  |  | FALSE |  | FALSE
DP3 | SV7T | Overcurrent Trip | Display Points | Alarm |  |  | FALSE |  | FALSE
DP3_1 | OC TRIP | Overcurrent Trip | Display Points | Alarm |  |  | FALSE |  | FALSE
DP3_0 | NA | Overcurrent Trip | Display Points | Alarm |  |  | FALSE |  | FALSE
DP4 | SV8T | MOV Failure | Display Points | Alarm |  |  | FALSE |  | FALSE
DP4_1 | MOV FAIL | MOV Failure | Display Points | Alarm |  |  | FALSE |  | FALSE
DP4_0 | NA | MOV Failure | Display Points | Alarm |  |  | FALSE |  | FALSE
DP5 | SV9T | Trip Coil Monitor | Display Points | Alarm |  |  | FALSE |  | FALSE
DP5_1 | LOR TC FAIL | Trip Coil Monitor | Display Points | Alarm |  |  | FALSE |  | FALSE
DP5_0 | NA | Trip Coil Monitor | Display Points | Alarm |  |  | FALSE |  | FALSE
ER | SV5+SV6+SV7+SV8 | Event Report Triggers | Report | Event |  |  | FALSE |  | FALSE
PROTO | SEL | Port Protocol | Communications | Port F |  |  | FALSE | PF | FALSE
SPEED | 19200 | Baud Rate | Communications | Port F |  |  | FALSE | PF | FALSE
PROTO | SEL | Port Protocol | Communications | Port 1 |  |  | FALSE | P1 | FALSE
SPEED | 19200 | Baud Rate | Communications | Port 1 |  |  | FALSE | P1 | FALSE

## MTR_735
SEL-735 Meter Settings & Logic
Relay Specification
Manufacturer | SEL
Model | SEL-735
Part # | 0735BX20944CFXB4XX16101XX
Function | Metering
Front View |  | Side View |  | Rear View
Relay Classification
Meter ID (MID) | Setpoint Class | Logic Class | IP Address (IPADDR)
REVMTR1 | A | 1 | 172.31.100.175
MTR1 | A | 1 | 172.31.100.176
MTR2 | B | 1 | 172.31.100.177
I/O Summary
I/O | Description
OUT103 | Meter Alarm to DPAC
Settings Table
Setting | Value | Description | Category | Function | Setpoint Class | Logic Class | Float | QuickSet Group | SER
TID | GRVR HL WND | Terminal Identifier | Identifier and Scaling | General |  |  | FALSE |  | FALSE
CTR | 40 | CT Ratio | Identifier and Scaling | Ratio | A |  | FALSE |  | FALSE
CTR | 500 | CT Ratio | Identifier and Scaling | Ratio | B |  | FALSE |  | FALSE
CTR | 240 | CT Ratio | Identifier and Scaling | Ratio | C |  | FALSE |  | FALSE
CTR | 240 | CT Ratio | Identifier and Scaling | Ratio | D |  | FALSE |  | FALSE
PTR | 700 | PT Ratio | Identifier and Scaling | Ratio | A |  | FALSE |  | FALSE
PTR | 175 | PT Ratio | Identifier and Scaling | Ratio | B |  | FALSE |  | FALSE
PTR | 175 | PT Ratio | Identifier and Scaling | Ratio | C |  | FALSE |  | FALSE
PTR | 175 | PT Ratio | Identifier and Scaling | Ratio | D |  | FALSE |  | FALSE
VOLT_SCA | KILO | Voltage Scaling | Identifier and Scaling | General |  |  | FALSE |  | FALSE
POWR_SCA | MEGA | Power and Demand Scaling | Identifier and Scaling | General |  |  | FALSE |  | FALSE
ENRG_SCA | MEGA | Energy Scaling | Identifier and Scaling | General |  |  | FALSE |  | FALSE
UTC_OFF | -5 | UTC Offset to Local Time | Global | Time |  |  | TRUE |  | FALSE
SRATE | 128 | Waveform Capture Sample Rate (Samples per Cycle) | Events & Logging | Event |  |  | FALSE |  | FALSE
LER | 120 | Event Length (cycles) | Events & Logging | Event |  |  | FALSE |  | FALSE
PRE | 15 | Prefault Length (cycles) | Events & Logging | Event |  |  | FALSE |  | FALSE
EPORT | Y | Enable Port | Communications | Port F |  |  | FALSE | PF | FALSE
PROTO | SEL | Port Protocol | Communications | Port F |  |  | FALSE | PF | FALSE
SPEED | 19200 | Baud Rate | Communications | Port F |  |  | FALSE | PF | FALSE
EPORT | Y | Enable Port | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ETELNET | Y | Enable Telnet | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EMODBUS | N | Enable Modbus | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EFTPSERV | N | Enable FTP | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EDNP | 2 | Enable DNP | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EPMIP | 0 | Enable PMU | Communications | Port 1 |  |  | FALSE | P1 | FALSE
TPORT | 23 | Telnet Port | Communications | Port 1 |  |  | FALSE | P1 | FALSE
SUBNETM | 255.255.255.0 | Subnet Mask | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DEFRTR | 172.31.100.254 | Default Router Gateway | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPNUM | 20000 | DNP TCP Port | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPADR | 1 | DNP Address | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPMAP | 1 | DNP Session Map | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPIP | 172.31.100.241 | DNP Master IP Address | Communications | Port 1 |  |  | FALSE | P1 | FALSE
REPADR | 0 | DNP Master IP Address | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DECPLA | 0 | Amps Scaling | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DECPLV | 0 | Voltages Scaling | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DECPLM | 0 | Misc. Data Scaling | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DECPLE | 0 | Energy Data Scaling | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ANADBA | 0 | Deadband Amps | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ANADBV | 0 | Deadband Volts | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ANADBM | 0 | Deadband Misc | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPMAP2 | 1 | DNP Session Map | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPIP2 | 172.31.100.243 | DNP Master IP Address | Communications | Port 1 |  |  | FALSE | P1 | FALSE
REPADR2 | 0 | DNP Master IP Address | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DECPLA2 | 0 | Amps Scaling | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DECPLV2 | 0 | Voltages Scaling | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DECPLM2 | 0 | Misc. Data Scaling | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DECPLE2 | 0 | Energy Data Scaling | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ANADBA2 | 0 | Deadband Amps | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ANADBV2 | 0 | Deadband Volts | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ANADBM2 | 0 | Deadband Misc | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EPORT | N | Enable Port 2 | Communications | Port 2 |  |  | FALSE | P2 | FALSE
EPORT | N | Enable Port 3 | Communications | Port 3 |  |  | FALSE | P3 | FALSE
EPORT | N | Enable Port 4 | Communications | Port 4 |  |  | FALSE | P4 | FALSE
BI_MAP1 | 0 2 3 4 5 6 7 1600 1601 1602 | Binary Input Map | Communications | DNP |  |  | FALSE | D | FALSE
AI_MAP1 | 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 200 3000 | Analog Input Map | Communications | DNP |  |  | FALSE | D | FALSE
CO_MAP1 | 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28 | Counter Map | Communications | DNP |  |  | FALSE | D | FALSE

## DPAC_2440
SEL-2440 DPAC Settings & Logic
Relay Specification
Manufacturer | SEL
Model | SEL-2440
Part # | 24402H11A1A11630
Function | DPAC
Front View |  |  |  | Rear View
Relay Classification
Device ID (DID) | Setpoint Class | Logic Class | IP Address (IPADDR)
DPAC1 | A | 1 | 172.31.100.120
DPAC2 | A | 2 | 172.31.100.121
I/O Summary
I/O | Description
See project schematics.
Settings Table
Setting | Value | Description | Category | Function | Setpoint Class | Logic Class | Float | QuickSet Group | SER
TID | GRVR HL WND | Terminal ID | General | Device |  |  | FALSE |  | FALSE
OUT101 | SV01T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT102 | SV02T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT103 | SV03T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT104 | SV04T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT105 | SV05T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT106 | SV06T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT107 | SV07T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT108 | SV08T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT109 | SV09T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT110 | SV10T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT111 | SV11T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT112 | SV12T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT113 | SV13T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT114 | SV14T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT115 | SV15T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT116 | SV16T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
EPORT | Y | Port Protocol | Communications | Port F |  |  | FALSE | PF | FALSE
SPEED | 19200 | Baud Rate | Communications | Port F |  |  | FALSE | PF | FALSE
EPORT | Y | Enable Port | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ETELNET | Y | Enable Telnet | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EFTP | N | Enable FTP | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EPING | Y | Enable Ping | Communications | Port 1 |  |  | FALSE | P1 | FALSE
SUBNETM | 255.255.255.0 | Subnet Mask | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DEFRTR | 172.31.100.254 | Default Router Gateway | Communications | Port 1 |  |  | FALSE | P1 | FALSE
ETCPKA | Y | Enable TCP Keep-Alive | Communications | Port 1 |  |  | FALSE | P1 | FALSE
KAIDLE | 10 | TCP KA Idle Range (sec) | Communications | Port 1 |  |  | FALSE | P1 | FALSE
KAINTV | 10 | TCP KA Interval Range (sec) | Communications | Port 1 |  |  | FALSE | P1 | FALSE
KACNT | 5 | TCP KA Count Range | Communications | Port 1 |  |  | FALSE | P1 | FALSE
TPORT | 23 | Telnet Port | Communications | Port 1 |  |  | FALSE | P1 | FALSE
NETMODE | FAILOVER | Port Operating Mode | Communications | Port 1 |  |  | FALSE | P1 | FALSE
NETPORT | A | Primary Port | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EDNP | 2 | Enable DNP Session | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPADR | 1 | DNP Address | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPIP1 | 172.31.100.241 | DNP Client IP | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPNUM1 | 20000 | DNP TCP Port | Communications | Port 1 |  |  | FALSE | P1 | FALSE
REPADR1 | 0 | Client DNP Address | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPMAP1 | 1 | DNP Map | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DVARAI1 | 5 | DNP Analog Input Variation | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DVARAIE1 | 5 | DNP Analog Input Variation | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPIP2 | 172.31.100.243 | DNP Client IP | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPNUM2 | 20000 | DNP TCP Port | Communications | Port 1 |  |  | FALSE | P1 | FALSE
REPADR2 | 0 | Client DNP Address | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DNPMAP2 | 1 | DNP Map | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DVARAI2 | 5 | DNP Analog Input Variation | Communications | Port 1 |  |  | FALSE | P1 | FALSE
DVARAIE2 | 5 | DNP Analog Input Variation | Communications | Port 1 |  |  | FALSE | P1 | FALSE
EPORT | N | Enable Port 2 | Communications | Port 2 |  |  | FALSE | P2 | FALSE
EPORT | N | Enable Port 3 | Communications | Port 3 |  |  | FALSE | P3 | FALSE
BI_00 | ENABLED | Relay Enabled | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_01 | IRIGOK | IRIG Status | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_02 | IN201 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_03 | IN202 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_04 | IN203 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_05 | IN204 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_06 | IN205 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_07 | IN206 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_08 | IN207 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_09 | IN208 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_10 | IN209 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_11 | IN210 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_12 | IN211 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_13 | IN212 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_14 | IN213 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_15 | IN214 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_16 | IN215 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_17 | IN216 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_18 | IN301 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_19 | IN302 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_20 | IN303 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_21 | IN304 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_22 | IN305 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_23 | IN306 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_24 | IN307 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_25 | IN308 | I/O | Communications | DNP |  |  | FALSE | D1 | FALSE
BI_26 | IN309 | I/O | Communications | DNP |  | 1 | FALSE | D1 | FALSE
BI_27 | IN310 | I/O | Communications | DNP |  | 1 | FALSE | D1 | FALSE
BI_28 | IN311 | I/O | Communications | DNP |  | 1 | FALSE | D1 | FALSE
BI_29 | IN312 | I/O | Communications | DNP |  | 1 | FALSE | D1 | FALSE
BI_30 | IN313 | I/O | Communications | DNP |  | 1 | FALSE | D1 | FALSE
BI_33 | IN316 | I/O | Communications | DNP |  | 1 | FALSE | D1 | FALSE
BI_26 | IN316 | I/O | Communications | DNP |  | 2 | FALSE | D1 | FALSE

## Line_GE L90
SEL-411L Line Protection Settings & Logic
Relay Specification
Manufacturer | GE
Model | GE L90
Part # | L90-TB5-HLH-F8L-H6P-L8L-N6S-S6S-U6D-W7K
Function | Line Protection
Front View |  |  |  | Rear View
Relay Classification
Relay ID (RID) | Setpoint Class | Logic Class | IP Address/CIDR (IPADDR)
87LP | A | 1 | 172.31.100.70
I/O Summary |  |  | Remote Bit Summary
I/O | Description |  | Element | Description | Behavior
IN/OUT | Description |  | RB1 | Target Reset | Pulse
IN201 | 52L Status (a)
IN202 | 89L Status (a)
IN203 | 86DTT Status |  | Pushbutton Summary
IN204 | 86DTT Trip Coil Monitor |  | Element | Description | Target LED
IN205 | Incoming BF TT |  | PB1 | Local 87L BLOCK | PB1_LED
IN206 | Not Used |  | PB2 | DTT Tx BLOCK | PB2_LED
IN207 | Not Used |  | PB3 | DTT Rx BLOCK | PB3_LED
IN208 | Not Used |  | PB4 | 87L TEST MODE | PB4_LED
OUT201 | 52L Protection Trip (TC1) |  | PB5 | DTT RECVD Indication | PB5_LED
OUT202 | Not Used |  | PB6 | DTT SENT Indication | PB6_LED
OUT203 | 86DTT Lockout Trip |  | PB7 | BKR 52L Status (Grn/Open) | PB7_LED
OUT204 | Breaker Failure Initiate |  | PB8 | SW 89L Status (Grn/Open) | PB8_LED
OUT205 | Not Used |  | PB9 | REMOTE 87L BLOCK | PB9_LED
OUT206 | Spare |  | PB10 | REMOTE TERMINAL (Grn/Open) | PB10LED
OUT207 | Not Used |  | PB11 | 86DTT TCM FAIL (Push to Reset) | PB11LED
OUT208 | Not Used |  | PB12 | Not Used | PB12LED
OUT209 | Not Used
OUT210 | Not Used
OUT211 | Not Used |  | Ratios & Nominal Voltages
OUT212 | Not Used |  | Element | Value
OUT213 | Not Used |  | CT Ratio | 600
OUT214 | Relay Fail Alarm |  | PT Ratio | 2000
OUT215 | Not Used |  | Collector Voltage (LL, kV) | 230
IN301 | Not Used |  | Relay Nominal Voltage (LL, Vsec) | 115
IN302 | Not Used
IN303 | Not Used
IN304 | Not Used
IN305 | Not Used
IN306 | Not Used
IN307 | Not Used
IN308 | Not Used
OUT301 | Not Used
OUT302 | Not Used
OUT303 | Not Used
OUT304 | Not Used
OUT305 | Not Used
OUT306 | Not Used
OUT307 | Not Used
OUT308 | Not Used
OUT309 | Not Used
OUT310 | Not Used
OUT311 | Not Used
OUT312 | Not Used
OUT313 | Not Used
OUT314 | Not Used
OUT315 | Not Used
Channel TX/RX Addresses
CH Address | Local | Remote
Channel_1 TA_1 | 2 | 1
Channel_1 RA_1 | 1 | 2
Line Impedence
Impedance Type | Magnitude (Ω_Sec) | Magnitude (Ω_Pri) | Angle (Degree)
Positive sequence line impedance | 0.494 | 1.6469 | 85.69
Zero sequence line impedance | 1.703 | 5.676 | 79.19
Settings Table
Setting | Value | Description | Category | Function | Setpoint Class | Logic Class | Float | QuickSet Group | SER
SID | GRVR HL WND | Station Identifier | Global | General |  |  | FALSE |  | FALSE
CONAM | AEP | Company Name | Global | General |  |  | FALSE |  | FALSE
NFREQ | 60 | Nominal Frequency (Hz) | Global | General |  |  | FALSE |  | FALSE
PHROT | ABC | Phase Rotation | Global | General |  |  | FALSE |  | FALSE
BID1 | 52L | Breaker 1 Identifier | Global | General |  |  | FALSE |  | FALSE
SS1 | 1 | Settings Group 1 Enable | Global | Enable |  |  | FALSE |  | FALSE
SS2 | 0 | Settings Group 2 Enable | Global | Enable |  |  | FALSE |  | FALSE
SS3 | 0 | Settings Group 3 Enable | Global | Enable |  |  | FALSE |  | FALSE
SS4 | 0 | Settings Group 4 Enable | Global | Enable |  |  | FALSE |  | FALSE
SS5 | 0 | Settings Group 5 Enable | Global | Enable |  |  | FALSE |  | FALSE
SS6 | 0 | Settings Group 6 Enable | Global | Enable |  |  | FALSE |  | FALSE
IRIGC | C37.118 | IRIG Control Bits Definition | Global | Time |  |  | FALSE |  | FALSE
UTCOFF | -5 | UTC Offset to Local Time | Global | Time |  |  | TRUE |  | FALSE
EDRSTC | Y | Enable Date Reset Control | Global | Data Reset Control |  |  | FALSE |  | FALSE
RSTTRGT | RB15 | Target Reset | Global | Data Reset Control |  |  | FALSE |  | FALSE
E87CH | 2SD | Enable 87L Channel (2 Terminal, Redundant Channel) | Port 87 | Enable |  |  | FALSE |  | FALSE
E87PG | P | Enable Tx/Rx Addresses and 87L Transmit Bits in Group Settings | Port 87 | Enable |  |  | FALSE |  | FALSE
87PCH | 1 | 87L Primary Serial Channel | Port 87 | Channel Config |  |  | FALSE |  | FALSE
87TADR | 1 | Relay Transmit Address | Port 87 | Channel Config |  |  | FALSE |  | FALSE
87R1ADR | 2 | Channel 1 Receive Address | Port 87 | Channel Config |  |  | FALSE |  | FALSE
52AA1 | IN201 | BK1 Contact Input | Breaker Monitor | Breaker 1 |  |  | FALSE |  | FALSE
CTRW | 600 | CT Ratio, Terminal W | Line Configuration | Ratios |  |  | FALSE |  | FALSE
PTRY | 2000 | PT Ratio, Terminal Y | Line Configuration | Ratios |  |  | FALSE |  | FALSE
VNOMY | 115 | PT Nominal Voltage (LL, Vsec) | Line Configuration | Ratios |  |  | FALSE |  | FALSE
Z1MAG | 0.494 | Pos Seq Line Impedance Mag | Line Configuration | Line Impedance |  |  | TRUE |  | FALSE
Z1ANG | 85.69 | Pos Seq Line Impedance Angle | Line Configuration | Line Impedance |  |  | TRUE |  | FALSE
Z0MAG | 1.703 | 0 Seq Line Impendance Mag | Line Configuration | Line Impedance |  |  | TRUE |  | FALSE
Z0ANG | 79.19 | 0 Seq Line Impedance Ang | Line Configuration | Line Impedance |  |  | TRUE |  | FALSE
E87L | Y | Enable Line Current Differential Protection 87L | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E87LCC | N | Enable Line Charging Current Compensation | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E87XFMR | N | Enable in Line Transformer Differential Protection | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E87OCTL | Y | Enable Open CT Detection Logic | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E21MP | 2 | Enable Mho Phase Distance Zones | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E21XP | N | Enable Quadrilateral Phase Distance Zones | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E21MG | 2 | Enable Mho Ground Distance Zones | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E21XG | N | Enable Quadrilateral Ground Distance Zones | Relay Configuration | Enable |  |  | FALSE |  | FALSE
ECVT | Y | Enable CVT Transient Detection | Relay Configuration | Enable |  |  | FALSE |  | FALSE
ESERCMP | N | Enable Series-Compensated Line Logic | Relay Configuration | Enable |  |  | FALSE |  | FALSE
ECDTD | Y | Enable Distance Element Common Time Delay | Relay Configuration | Enable |  |  | FALSE |  | FALSE
ESOTF | Y | Enable Switch-Onto-Fault | Relay Configuration | Enable |  |  | FALSE |  | FALSE
EOOS | N | Enable Out-of-Step | Relay Configuration | Enable |  |  | FALSE |  | FALSE
ELOAD | N | Enable Load Encroachment | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E50P | N | Enable Phase Instantaneous/Definite-Time Overcurrent Elements | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E50G | 1 | Enable Residual Ground Instantaneous/Definite-Time Overcurrent Elements | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E50Q | N | Enable Negative-Sequence Instantaneous/Definite-Time Overcurrent Elements | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E51 | N | Enable Inverse Time Overcurrent Elements | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E81 | N | Enable Frequency Elements | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E27 | N | Enable Under Voltage Elements | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E59 | N | Enable Over Voltage Elements | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E32P | N | Enable Over/Under Power Elements | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E32 | Y | Enable Directional Control | Relay Configuration | Enable |  |  | FALSE |  | FALSE
ETHRIEC | N | Enable IEC Thermal Element | Relay Configuration | Enable |  |  | FALSE |  | FALSE
ECOMM | N | Enable Communication Scheme | Relay Configuration | Enable |  |  | FALSE |  | FALSE
EBCD | N | Enable Broken Conductor Detection | Relay Configuration | Enable |  |  | FALSE |  | FALSE
EBFL1 | N | Enable Breaker 1 Failure Logic | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E25BK1 | N | Enable Synchronism Check for Breaker 1 | Relay Configuration | Enable |  |  | FALSE |  | FALSE
E79 | N | Enable Reclosing | Relay Configuration | Enable |  |  | FALSE |  | FALSE
EMANCL | N | Enable Manual Closing | Relay Configuration | Enable |  |  | FALSE |  | FALSE
ELOP | Y1 | Enable Loss-of-Potential | Relay Configuration | Enable |  |  | FALSE |  | FALSE
EDEM | N | Enable Demand Metering | Relay Configuration | Enable |  |  | FALSE |  | FALSE
EADVS | Y | Enable Advanced Settings | Relay Configuration | Enable |  |  | FALSE |  | FALSE
VMEMC | 0 | Memory Voltage Control Equation (SELogic) | Relay Configuration | Enable |  |  | FALSE |  | FALSE
EFID | N | Enable FID Logic | Relay Configuration | Enable |  |  | FALSE |  | FALSE
k0M1 | 0.882 | Zone 1 ZSC Factor Magnitude | Zero-Sequence Compensation Factor | Compensation Factor |  |  | TRUE |  | FALSE
k0A1 | -14.671 | Zone 1 ZSC Factor Angle (deg) | Zero-Sequence Compensation Factor | Compensation Factor |  |  | TRUE |  | FALSE
k0M | 0.882 | Forward Zones ZSC Factor Magnitude | Zero-Sequence Compensation Factor | Compensation Factor |  |  | TRUE |  | FALSE
k0A | -14.671 | Forward Zones ZSC Factor Angle (deg) | Zero-Sequence Compensation Factor | Compensation Factor |  |  | TRUE |  | FALSE
k0MR | 0.882 | Reverse Zones ZSC Factor Magnitude | Zero-Sequence Compensation Factor | Compensation Factor |  |  | TRUE |  | FALSE
k0AR | -14.671 | Reverse Zones ZSC Factor Angle (deg) | Zero-Sequence Compensation Factor | Compensation Factor |  |  | TRUE |  | FALSE
87LPP | 1.2 | Phase 87L Pickup (pu) | Differential | 87L |  |  | TRUE |  | FALSE
87LPR | 6 | Outer Radius | Differential | 87L |  |  | TRUE |  | FALSE
87LPA | 195 | Restraint Region | Differential | 87L |  |  | FALSE |  | FALSE
87LPPS | 1.44 | Pickup in Secure Mode | Differential | 87L |  |  | TRUE |  | FALSE
87LPRS | 7.2 | Outer Radius in Secure Mode | Differential | 87L |  |  | TRUE |  | FALSE
87LPAS | 234 | Restraint Region in Secure Mode | Differential | 87L |  |  | FALSE |  | FALSE
87LGP | 0.25 | Ground 87L Pickup (pu) | Differential | 87L |  |  | TRUE |  | FALSE
87LGR | 6 | Outer Radius | Differential | 87L |  |  | TRUE |  | FALSE
87LGA | 195 | Restraint Region | Differential | 87L |  |  | FALSE |  | FALSE
87LGPS | 0.3 | Pickup in Secure Mode | Differential | 87L |  |  | TRUE |  | FALSE
87LGRS | 7.2 | Outer Radius in Secure Mode | Differential | 87L |  |  | TRUE |  | FALSE
87LGAS | 234 | Restraint Region in Secure Mode | Differential | 87L |  |  | FALSE |  | FALSE
Z1MP | 0.4 | Zone 1 Reach (ohms, sec) | Distance | Phase Mho |  |  | TRUE |  | FALSE
Z1MPTC | 1 | Zone 1 Torque Control | Distance | Phase Mho |  |  | FALSE |  | FALSE
Z2MP | 0.59 | Zone 2 Reach (ohms, sec) | Distance | Phase Mho |  |  | TRUE |  | FALSE
Z2MPTC | 1 | Zone 2 Torque Control | Distance | Phase Mho |  |  | FALSE |  | FALSE
Z1MG | 0.4 | Zone 1 Reach (ohms, sec) | Distance | Ground Mho |  |  | TRUE |  | FALSE
Z1MGTC | 1 | Zone 1 Torque Control | Distance | Ground Mho |  |  | FALSE |  | FALSE
Z2MG | 0.59 | Zone 2 Reach (ohms, sec) | Distance | Ground Mho |  |  | TRUE |  | FALSE
Z2MGTC | 1 | Zone 2 Torque Control | Distance | Ground Mho |  |  | FALSE |  | FALSE
Z1D | 0 | Common Zone 1 Time Delay (cyc) | Distance | Common Mho |  |  | TRUE |  | FALSE
Z2D | 18 | Common Zone 2 Time Delay (cyc) | Distance | Common Mho |  |  | TRUE |  | FALSE
50G1P | 0.25 | Level 1 Residual Ground Inst OC Pickup (A-sec) | Overcurrent | Ground OC |  |  | TRUE |  | FALSE
67G1D | 0 | Level 1 Residual Ground Inst OC Time Delay (cyc) | Overcurrent | Ground OC |  |  | TRUE |  | FALSE
67G1TC | 1 | Level 1 Residual Ground Inst OC Torque Control | Overcurrent | Ground OC |  |  | FALSE |  | FALSE
TR | (87OP AND NOT 87LST) OR Z1T OR Z2T OR 67G1T | Trip Conditions | Trip Logic | Trip |  |  | FALSE |  | TRUE
ULTR | TRGTR | Unlatch Trip | Trip Logic | Trip |  |  | FALSE |  | FALSE
DTA | PSV02 AND NOT PLT03 | Direct Transfer Trip A-Phase | Trip Logic | DTT |  |  | FALSE |  | FALSE
DTB | PSV02 AND NOT PLT03 | Direct Transfer Trip B-Phase | Trip Logic | DTT |  |  | FALSE |  | FALSE
DTC | PSV02 AND NOT PLT03 | Direct Transfer Trip C-Phase | Trip Logic | DTT |  |  | FALSE |  | FALSE
TDUR3D | 9 | Min Trip Duration (cyc) | Trip Logic | Trip |  |  | TRUE |  | FALSE
ER | R_TRIG Z1P OR R_TRIG Z1G OR R_TRIG PSV01 OR R_TRIG PSV02 OR R_TRIG 3PT OR R_TRIG 87BLK OR R_TRIG 87LST OR R_TRIG IN205 | Event Report Triggers | Trip Logic | Event |  |  | FALSE |  | TRUE
OUT201 | 3PT | Three Pole Trip | Outputs | Trip |  |  | FALSE |  | TRUE
OUT202 | NA | Not Used | Outputs |  |  |  | FALSE |  | TRUE
OUT203 | PSV02 AND NOT PLT03 | 86DTT Trip | Outputs | Trip |  |  | FALSE |  | TRUE
OUT204 | 3PT | BFI | Outputs | Breaker Failure |  |  | FALSE |  | TRUE
OUT214 | NOT (SALARM OR HALARM) | Relay Fail Alarm | Outputs | Alarm |  |  | FALSE |  | FALSE
DP_ELE1 |  |  | Display Points | Indication |  |  | FALSE |  | FALSE
PROTSEL1 | PSV01 := NOT PLT02 AND IN205 | DTT Trigger | Variables | DTT |  |  | FALSE |  | TRUE
PROTSEL2 | PSV02 := (87CH1OK AND 87R01P1) OR (87CH2OK AND 87R01P2) | DTT Request Received | Variables | DTT |  |  | FALSE |  | TRUE
PROTSEL3 | PSV03 := (87CH1OK AND 87R06P1) OR (87CH2OK AND 87R06P2) | Remote 87L Block Request | Variables | 87L |  |  | FALSE |  | TRUE
PROTSEL4 | PSV04 := (87CH1OK AND 87R07P1) OR (87CH2OK AND 87R07P2) | Remote Terminal Status | Variables | 87L |  |  | FALSE |  | TRUE
PROTSEL5 | # | [5 empty] | FALSE |  | FALSE
PROTSEL6 | ########################### | [5 empty] | FALSE |  | FALSE
PROTSEL7 | PCT01DO := 1 | LOP Alarm | Timed Protection Variables | Alarm |  |  | FALSE |  | FALSE
PROTSEL8 | PCT01PU := 600 | LOP Alarm | Timed Protection Variables | Alarm |  |  | FALSE |  | FALSE
PROTSEL9 | PCT01IN := LOP | LOP Alarm | Timed Protection Variables | Alarm |  |  | FALSE |  | TRUE
PROTSEL10 | PCT02DO := 0.0 | 86DTT TCM Fail | Timed Protection Variables | Alarm |  |  | FALSE |  | FALSE
PROTSEL11 | PCT02PU := 30.0 | 86DTT TCM Fail | Timed Protection Variables | Alarm |  |  | FALSE |  | TRUE
PROTSEL12 | PCT02IN := NOT IN203 AND IN204 | 86DTT TCM Fail | Timed Protection Variables | Alarm |  |  | FALSE |  | FALSE
PROTSEL13 | # | [5 empty] | FALSE |  | FALSE
PROTSEL14 | # | [5 empty] | FALSE |  | FALSE
PROTSEL15 | # | [5 empty] | FALSE |  | FALSE
PROTSEL16 | # | [5 empty] | FALSE |  | FALSE
PROTSEL17 | # | [5 empty] | FALSE |  | FALSE
PROTSEL18 | # | [5 empty] | FALSE |  | FALSE
PROTSEL19 | # | [5 empty] | FALSE |  | FALSE
PROTSEL20 | # | [5 empty] | FALSE |  | FALSE
PROTSEL21 | # | [5 empty] | FALSE |  | FALSE
PROTSEL22 | ############################ | [5 empty] | FALSE |  | FALSE
PROTSEL23 | PLT01S := PB1_PUL AND NOT PLT01 | Local 87L Block (Set) | Protection Latches | Indication |  |  | FALSE |  | TRUE
PROTSEL24 | PLT01R := PB1_PUL AND PLT01 | Local 87L Block (Reset) | Protection Latches | Indication |  |  | FALSE |  | FALSE
PROTSEL25 | PLT02S := PB2_PUL AND NOT PLT02 | DTT Transmit Block (Set) | Protection Latches | Indication |  |  | FALSE |  | TRUE
PROTSEL26 | PLT02R := PB2_PUL AND PLT02 | DTT Transmit Block (Reset) | Protection Latches | Indication |  |  | FALSE |  | FALSE
PROTSEL27 | PLT03S := PB3_PUL AND NOT PLT03 | DTT Receive Block (Set) | Protection Latches | Indication |  |  | FALSE |  | TRUE
PROTSEL28 | PLT03R := PB3_PUL AND PLT03 | DTT Receive Block (Reset) | Protection Latches | Indication |  |  | FALSE |  | FALSE
PROTSEL29 | PLT04S := PB4_PUL AND NOT PLT04 | 87L Test Mode Enable (Set) | Protection Latches | Indication |  |  | FALSE |  | TRUE
PROTSEL30 | PLT04R := PB4_PUL AND PLT04 | 87L Test Mode Enable (Reset) | Protection Latches | Indication |  |  | FALSE |  | FALSE
PROTSEL31 | PLT05S := PSV02 AND NOT PLT05 | DTT Received Indication (Set) | Protection Latches | Indication |  |  | FALSE |  | TRUE
PROTSEL32 | PLT05R := NOT PSV02 AND TRGTR AND PLT05 | DTT Received Indication (Reset) | Protection Latches | Indication |  |  | FALSE |  | FALSE
PROTSEL33 | PLT06S := PSV01 AND NOT PLT06 | DTT Transmitted Indication (Set) | Protection Latches | Indication |  |  | FALSE |  | TRUE
PROTSEL34 | PLT06R := NOT PSV01 AND TRGTR AND PLT06 | DTT Transmitted Indication (Reset) | Protection Latches | Indication |  |  | FALSE |  | FALSE
PROTSEL35 | PLT07S := PCT02Q AND NOT PLT07 | 86DTT TCM Fail (Set) | Protection Latches | Indication |  |  | FALSE |  | TRUE
PROTSEL36 | PLT07R := NOT PCT02Q AND PB11PUL AND PLT07 | 86DTT TCM Fail (Reset) | Protection Latches | Indication |  |  | FALSE |  | FALSE
PROTSEL37 | # | [5 empty] | FALSE |  | FALSE
PROTSEL38 | # | [5 empty] | FALSE |  | FALSE
PROTSEL39 | # | [5 empty] | FALSE |  | FALSE
PROTSEL40 | # | [5 empty] | FALSE |  | FALSE
PROTSEL41 | # | [5 empty] | FALSE |  | FALSE
PROTSEL42 | # | [5 empty] | FALSE |  | FALSE
PROTSEL43 | ############################ | [5 empty] | FALSE |  | FALSE
PROTSEL44 | # | [5 empty] | FALSE |  | FALSE
PROTSEL45 | # | [5 empty] | FALSE |  | FALSE
PROTSEL46 | # | [5 empty] | FALSE |  | FALSE
PROTSEL47 | # | [5 empty] | FALSE |  | FALSE
PROTSEL48 | # | [5 empty] | FALSE |  | FALSE
PROTSEL49 | # | [5 empty] | FALSE |  | FALSE
PROTSEL50 | # | [5 empty] | FALSE |  | FALSE
87T1P1 | PSV01 | Direct Transfer Trip | 87L Communication Bits | 87L |  |  | FALSE |  | FALSE
87T2P1 | PLT01 | Local 87L Block | 87L Communication Bits | 87L |  |  | FALSE |  | FALSE
87T3P1 | NOT IN201 OR NOT IN202 | Local Terminal Open | 87L Communication Bits | 87L |  |  | FALSE |  | FALSE
T1_LED | (87OP OR 87DTTI) AND NOT (SOTFT OR TLED_3) | Instantaneous Diff Trip | LED | Indication |  |  | FALSE |  | FALSE
T1EDL | Y | Instantaneous Diff Trip | LED | Indication |  |  | FALSE |  | FALSE
T1EDC | RO | Instantaneous Diff Trip | LED | Indication |  |  | FALSE |  | FALSE
T2_LED | Z1PT OR Z1GT | Zone 1 Timed Trip | LED | Indication |  |  | FALSE |  | FALSE
T2EDL | Y | Zone 1 Timed Trip | LED | Indication |  |  | FALSE |  | FALSE
T2EDC | RO | Zone 1 Timed Trip | LED | Indication |  |  | FALSE |  | FALSE
T3_LED | COMPRM AND NOT (Z1P OR Z1G OR TLED_1 OR SOTFT) | Communications Trip | LED | Indication |  |  | FALSE |  | FALSE
T3EDL | Y | Communications Trip | LED | Indication |  |  | FALSE |  | FALSE
T3EDC | RO | Communications Trip | LED | Indication |  |  | FALSE |  | FALSE
T4_LED | SOTFT | Switch onto Fault | LED | Indication |  |  | FALSE |  | FALSE
T4EDL | Y | Switch onto Fault | LED | Indication |  |  | FALSE |  | FALSE
T4EDC | RO | Switch onto Fault | LED | Indication |  |  | FALSE |  | FALSE
T5_LED | (Z1P OR Z1G) AND NOT (TLED_6 OR TLED_7 OR TLED_8) | Zone 1 Trip | LED | Indication |  |  | FALSE |  | FALSE
T5EDL | Y | Zone 1 Trip | LED | Indication |  |  | FALSE |  | FALSE
T5EDC | RO | Zone 1 Trip | LED | Indication |  |  | FALSE |  | FALSE
T6_LED | (Z2P OR Z2G) AND NOT (Z1P OR Z1G OR TLED_5 OR TLED_7) | Zone 2 Trip | LED | Indication |  |  | FALSE |  | FALSE
T6EDL | N | Zone 2 Trip | LED | Indication |  |  | FALSE |  | FALSE
T6EDC | RO | Zone 2 Trip | LED | Indication |  |  | FALSE |  | FALSE
T7_LED | (Z3P OR Z3G) AND NOT (TLED_5 OR TLED_6 OR TLED_8) | Zone 3 Trip | LED | Indication |  |  | FALSE |  | FALSE
T7EDL | N | Zone 3 Trip | LED | Indication |  |  | FALSE |  | FALSE
T7EDC | RO | Zone 3 Trip | LED | Indication |  |  | FALSE |  | FALSE
T8_LED | (Z4P OR Z4G) AND NOT (Z1P OR Z2P OR Z3P OR Z1G OR Z2G OR Z3G OR TLED_5 OR TLED_6 OR TLED_7) | Zone 4 Trip | LED | Indication |  |  | FALSE |  | FALSE
T8EDL | N | Zone 4 Trip | LED | Indication |  |  | FALSE |  | FALSE
T8EDC | RO | Zone 4 Trip | LED | Indication |  |  | FALSE |  | FALSE
T9_LED | (PHASE_A AND NOT 87FTS) OR FTSA | Phase A Trip | LED | Indication |  |  | FALSE |  | FALSE
T9EDL | Y | Phase A Trip | LED | Indication |  |  | FALSE |  | FALSE
T9EDC | RO | Phase A Trip | LED | Indication |  |  | FALSE |  | FALSE
T10_LED | (PHASE_B AND NOT 87FTS) OR FTSB | Phase B Trip | LED | Indication |  |  | FALSE |  | FALSE
T10EDL | Y | Phase B Trip | LED | Indication |  |  | FALSE |  | FALSE
T10EDC | RO | Phase B Trip | LED | Indication |  |  | FALSE |  | FALSE
T11_LED | (PHASE_C AND NOT 87FTS) OR FTSC | Phase C Trip | LED | Indication |  |  | FALSE |  | FALSE
T11EDL | Y | Phase C Trip | LED | Indication |  |  | FALSE |  | FALSE
T11EDC | RO | Phase C Trip | LED | Indication |  |  | FALSE |  | FALSE
T12_LED | (GROUND AND NOT 87FTS) OR FTSG | Ground Trip | LED | Indication |  |  | FALSE |  | FALSE
T12EDL | Y | Ground Trip | LED | Indication |  |  | FALSE |  | FALSE
T12EDC | RO | Ground Trip | LED | Indication |  |  | FALSE |  | FALSE
T13_LED | 87OP OR 87DTTI | 87L Trip | LED | Indication |  |  | FALSE |  | FALSE
T13EDL | Y | 87L Trip | LED | Indication |  |  | FALSE |  | FALSE
T13EDC | RO | 87L Trip | LED | Indication |  |  | FALSE |  | FALSE
T14_LED | 87LST | 87L Not Available | LED | Indication |  |  | FALSE |  | FALSE
T14EDL | N | 87L Not Available | LED | Indication |  |  | FALSE |  | FALSE
T14EDC | RO | 87L Not Available | LED | Indication |  |  | FALSE |  | FALSE
T15_LED | 87CH1AL OR 87CH2AL OR 87CH3AL OR 87CH1FB OR 87CH2FB OR 87CH3FB | 87L Comm Fail Alarm | LED | Indication |  |  | FALSE |  | TRUE
T15EDL | N | 87L Comm Fail Alarm | LED | Indication |  |  | FALSE |  | FALSE
T15EDC | RO | 87L Comm Fail Alarm | LED | Indication |  |  | FALSE |  | FALSE
T16_LED | IN203 | 86DTT Lockout Operation | LED | Indication |  |  | FALSE |  | FALSE
T16EDL | N | 86DTT Lockout Operation | LED | Indication |  |  | FALSE |  | FALSE
T16EDC | RO | 86DTT Lockout Operation | LED | Indication |  |  | FALSE |  | FALSE
T17_LED | 87OCT | Open-Circuited CT Detected, Any Phase | LED | Indication |  |  | FALSE |  | TRUE
T17EDL | Y | Open-Circuited CT Detected, Any Phase | LED | Indication |  |  | FALSE |  | FALSE
T17EDC | RO | Open-Circuited CT Detected, Any Phase | LED | Indication |  |  | FALSE |  | FALSE
T18_LED | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T18EDL | N | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T18EDC | RO | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T19_LED | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T19EDL | N | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T19EDC | RO | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T20_LED | 0 | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T20EDL | N | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T20EDC | RO | Not Used | LED | Indication |  |  | FALSE |  | FALSE
T21_LED | 50P1 OR 50P2 OR 50P3 OR 50P4 OR 50Q1 OR 50Q2 OR 50Q3 OR 50Q4 OR 50G1 OR 50G2 OR 50G3 OR 50G4 | Instantaneous Overcurrent Trip | LED | Indication |  |  | FALSE |  | FALSE
T21EDL | Y | Instantaneous Overcurrent Trip | LED | Indication |  |  | FALSE |  | FALSE
T21EDC | RO | Instantaneous Overcurrent Trip | LED | Indication |  |  | FALSE |  | FALSE
T22_LED | 51T01 OR 51T02 OR 51T03 OR 51T04 OR 51T05 OR 51T06 OR 51T07 OR 51T08 OR 51T09 OR 51T10 | Timed Overcurrent Trip | LED | Indication |  |  | FALSE |  | FALSE
T22EDL | Y | Timed Overcurrent Trip | LED | Indication |  |  | FALSE |  | FALSE
T22EDC | RO | Timed Overcurrent Trip | LED | Indication |  |  | FALSE |  | FALSE
T23_LED | LOP | Loss of Potential | LED | Indication |  |  | FALSE |  | TRUE
T23EDL | N | Loss of Potential | LED | Indication |  |  | FALSE |  | FALSE
T23EDC | RO | Loss of Potential | LED | Indication |  |  | FALSE |  | FALSE
T24_LED | TIRIG | IRIG OK | LED | Indication |  |  | FALSE |  | TRUE
T24EDL | N | IRIG OK | LED | Indication |  |  | FALSE |  | FALSE
T24EDC | GO | IRIG OK | LED | Indication |  |  | FALSE |  | FALSE
ERDIG | A | Store Selected or All Relay Word Bits | Report | Event |  |  | FALSE |  | FALSE
SRATE | 2 | Sample Rate of Event Report (kHz) | Report | Event |  |  | FALSE |  | FALSE
LER | 1 | Length of Event Report (seconds) | Report | Event |  |  | TRUE |  | FALSE
PRE | 0.25 | Length of Pre-Fault (seconds) | Report | Event |  |  | TRUE |  | FALSE
SITM1 | TRIP | SER | Report | SER |  |  | FALSE |  | TRUE
SITM2 | 87OP | SER | Report | SER |  |  | FALSE |  | TRUE
SITM3 | 87LST | SER | Report | SER |  |  | FALSE |  | TRUE
SITM4 | Z1T | SER | Report | SER |  |  | FALSE |  | TRUE
SITM5 | Z2T | SER | Report | SER |  |  | FALSE |  | TRUE
SITM6 | 67G1T | SER | Report | SER |  |  | FALSE |  | TRUE
SITM7 | Z1P | SER | Report | SER |  |  | FALSE |  | TRUE
SITM8 | Z1G | SER | Report | SER |  |  | FALSE |  | TRUE
SITM9 | PSV01 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM10 | PSV02 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM11 | 3PT | SER | Report | SER |  |  | FALSE |  | TRUE
SITM12 | 87BLK | SER | Report | SER |  |  | FALSE |  | TRUE
SITM13 | IN205 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM14 | PSV03 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM15 | PSV04 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM16 | PCT01Q | SER | Report | SER |  |  | FALSE |  | TRUE
SITM17 | PCT02Q | SER | Report | SER |  |  | FALSE |  | TRUE
SITM18 | PLT01 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM19 | PLT02 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM20 | PLT03 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM21 | PLT04 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM22 | PLT05 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM23 | PLT06 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM24 | PLT07 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM25 | 87CH1AL | SER | Report | SER |  |  | FALSE |  | TRUE
SITM26 | 87CH2AL | SER | Report | SER |  |  | FALSE |  | TRUE
SITM27 | 87CH3AL | SER | Report | SER |  |  | FALSE |  | TRUE
SITM28 | 87CH1FB | SER | Report | SER |  |  | FALSE |  | TRUE
SITM29 | 87CH2FB | SER | Report | SER |  |  | FALSE |  | TRUE
SITM30 | 87CH3FB | SER | Report | SER |  |  | FALSE |  | TRUE
SITM31 | 87OCT | SER | Report | SER |  |  | FALSE |  | TRUE
SITM32 | LOP | SER | Report | SER |  |  | FALSE |  | TRUE
SITM33 | TIRIG | SER | Report | SER |  |  | FALSE |  | TRUE
SITM34 | IN201 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM35 | IN202 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM36 | IN203 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM37 | IN204 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM38 | OUT201 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM39 | OUT202 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM40 | OUT203 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM41 | OUT204 | SER | Report | SER |  |  | FALSE |  | TRUE
SITM42 | 87DTTI | SER | Report | SER |  |  | FALSE |  | TRUE
ERAQ1 | LIAFM | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ2 | LIBFM | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ3 | LICFM | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ4 | VAFM | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ5 | VBFM | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ6 | VCFM | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ7 | VABFM | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ8 | VBCFM | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ9 | VCAFM | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ10 | 3P_F | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ11 | 3Q_F | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
ERAQ12 | FREQ | Event Report Analog | Report | Event |  |  | FALSE |  | FALSE
EPORT | Y | Enable Port | Communications | Port F |  |  | FALSE | PF | FALSE
PROTO | SEL | Protocol | Communications | Port F |  |  | FALSE | PF | FALSE
SPEED | 19200 | Baud Rate | Communications | Port F |  |  | FALSE | PF | FALSE
EPORT | Y | Enable Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DEFRTR | 172.31.100.254 | Default Router | Communications | Port 5 |  |  | FALSE | P5 | FALSE
NETMODE | FAILOVER | Operating Mode | Communications | Port 5 |  |  | FALSE | P5 | FALSE
NETPORT | A | Primary Network Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ETELNET | Y | Enable Telnet | Communications | Port 5 |  |  | FALSE | P5 | FALSE
TPORT | 23 | Telnet Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
EDNP | 1 | Enable DNP Sessions | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPADR | 1 | DNP Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPPNUM | 20000 | DNP TCP Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPIP1 | 172.31.100.241 | DNP Client IP | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPTR1 | TCP | DNP Transport Protocol | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPMAP1 | 1 | DNP Session Map | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLA1 | 0 | Currents Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECVPLV1 | 0 | Voltages Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLM1 | 0 | Misc Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
AIVAR1 | 5 | Default Analog Input Variation | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBA1 | 0 | Deadband, Currents | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBV1 | 0 | Deadband, Voltages | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBM1 | 0 | Deadband, Misc | Communications | Port 5 |  |  | FALSE | P5 | FALSE
MINDIST | OFF | Min Fault Location to Capture | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
MAXDIST | OFF | Max Fault Location to Capture | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_1 | EN | Relay Enabled | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_2 | IN201 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_3 | IN202 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_4 | IN203 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_5 | IN205 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_6 | TLED_1 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_7 | TLED_2 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_8 | TLED_3 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_9 | TLED_4 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_10 | TLED_5 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_11 | TLED_6 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_12 | TLED_7 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_13 | TLED_8 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_14 | TLED_9 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_15 | TLED_10 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_16 | TLED_11 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_17 | TLED_12 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_18 | TLED_13 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_19 | TLED_14 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_20 | TLED_15 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_21 | TLED_16 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_22 | TLED_21 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_23 | TLED_22 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_24 | TLED_23 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_25 | TLED_24 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_26 | TRIPLED | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_1 | LIAFM | Current | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_2 | LIBFM | Current | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_3 | LICFM | Current | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_4 | VAFM | Voltage | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_5 | VBFM | Voltage | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_6 | VCFM | Voltage | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_7 | 3P_F | Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_8 | 3Q_F | Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_9 | DC1 | Battery Voltage | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_10 | FREQ | Frequency | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_1 | RB01 | Target Reset | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
Rear Views are not available from GE for the L90 Multilin due to the nature of the customizeable I/O modules.

## Line_411L
SEL-411L Line Protection Settings & Logic
Relay Specification
Manufacturer | SEL
Model | SEL-411L
Part # | 0411L1X6X5C8EEXH674740X
Function | Line Protection
Front View |  |  |  | Rear View
Relay Classification
Relay ID (RID) | Setpoint Class | Logic Class | IP Address/CIDR (IPADDR)
87LS | A | 1 | 172.31.100.71/24
I/O Summary |  |  | Remote Bit Summary
I/O | Description |  | Element | Description | Behavior
IN/OUT | Description |  | RB1 | Target Reset | Pulse
IN201 | 52T Status (a)
IN202 | 89L Status (a)
IN203 | 86DTT Status |  | Pushbutton Summary
IN204 | Spare |  | Element | Description | Target LED
IN205 | Incoming BF TT |  | PB1 | Local 87L BLOCK | PB1_LED
IN206 | Spare |  | PB2 | DTT Tx BLOCK | PB2_LED
IN207 | Not Used |  | PB3 | DTT Rx BLOCK | PB3_LED
IN208 | Not Used |  | PB4 | 87L TEST MODE | PB4_LED
OUT201 | 52T Protection Trip (TC1) |  | PB5 | DTT Received Indication | PB5_LED
OUT202 | Not Used |  | PB6 | DTT Sent Indication | PB6_LED
OUT203 | 86DTT Lockout Trip |  | PB7 | BKR 52T1 Status (Grn/Open) | PB7_LED
OUT204 | Breaker Failure Initiate |  | PB8 | SW 89L1 Status (Grn/Open) | PB8_LED
OUT205 | Not Used |  | PB9 | Remote 87L Block | PB9_LED
OUT206 | Spare |  | PB10 | Remote Terminal Closed | PB10LED
OUT207 | Not Used |  | PB11 | Remote Terminal Open | PB11LED
OUT208 | Not Used |  | PB12 | Event Manual Trigger | PB12LED
OUT209 | Not Used
OUT210 | Not Used
OUT211 | Not Used |  | Ratios & Nominal Voltages
OUT212 | Not Used |  | Terminal | Element | Value
OUT213 | Not Used |  | IW | CT Ratio | 400
OUT214 | Relay Fail Alarm |  |  | Line Voltage (kV-LL)
OUT215 | Not Used |  | VY | PT Ratio | 1200
IN301 | Not Used |  |  | Line Voltage (LL, kV) | 138
IN302 | Not Used |  |  | Relay Nominal Voltage (LL, Vsec) | 115
IN303 | Not Used
IN304 | Not Used
IN305 | Not Used
IN306 | Not Used
IN307 | Not Used
IN308 | Not Used
OUT301 | Not Used
OUT302 | Not Used
OUT303 | 87LS Fault Indicator
OUT304 | Not Used
OUT305 | Not Used
OUT306 | Not Used
OUT307 | Not Used
OUT308 | Not Used
OUT309 | Not Used
OUT310 | Not Used
OUT311 | Not Used
OUT312 | Not Used
OUT313 | Not Used
OUT314 | Not Used
OUT315 | Not Used
Channel TX/RX Addresses
CH Address | Local | Remote
87TADR | 4 | 3
87R1ADR | 3 | 4
Line Impedence
Impedance Type | Magnitude (Ω_Sec) | Magnitude (Ω_Pri) | Angle (Degree)
Positive sequence line impedance | 2.0222 | 6.0667 | 80.9516
Zero sequence line impedance | 4.966 | 14.8981 | 82.1682
Settings Table
Setting | Value | Description | Category | Function | Setpoint Class | Logic Class | Float | QuickSet Group | SER
SID | GRVR HL WND | Station Identifier | Global | General |  |  | FALSE | G1 | FALSE
RID | 87LS | Relay Identifier | Global | General |  |  | FALSE | G1 | FALSE
CONAM | AEP | Company Name | Global | General |  |  | FALSE | G1 | FALSE
BID1 | 52T1 | Breaker 1 Identifier | Global | General |  |  | FALSE | G1 | FALSE
FAULT | 51S01 OR Z2P OR Z2G OR 87LP OR 87LQ OR 87LG | Fault Condition Equation (SELogic) | Global | Trip |  |  | FALSE | G1 | FALSE
EGADVS | Y | Advanced Global Settings | Global | Enable |  |  | FALSE | G1 | FALSE
SS1 | 1 | Condition(s) to Enable Setting Group 1 (SELogic) | Global | Enable |  |  | FALSE | G1 | FALSE
SS2 | 0 | Condition(s) to Enable Setting Group 2 (SELogic) | Global | Enable |  |  | FALSE | G1 | FALSE
TGR | 300 | Group Change Delay (cyc) | Global | General |  |  | FALSE | G1 | FALSE
ESS | Y | Current and Voltage Source Selection | Global | General |  |  | FALSE | G1 | FALSE
IRIGC | C37.118 | IRIG-B Control Bits Definition | Global | Time |  |  | FALSE | G1 | FALSE
UTCOFF | -5.0 | Offset From UTC to Local Time | Global | Time |  |  | FALSE | G1 | FALSE
E87CH | 2SS | Enable 87L Channel | Port 87 | Enable |  |  | FALSE | P87 | FALSE
87TADR | 4 | Relay Transmit Address | Port 87 | Differential Comm |  |  | FALSE | P87 | FALSE
87R1ADR | 3 | Channel 1 Receive Address | Port 87 | Differential Comm |  |  | FALSE | P87 | FALSE
87CH1MT | OFF | Max. Round Trip Delay for Ch 1 (ms) | Port 87 | Differential |  |  | FALSE | P87 | FALSE
87CH1MD | OFF | Max. Step Change in Ch 1 Delay (ms) | Port 87 | Differential |  |  | FALSE | P87 | FALSE
87CH1MA | OFF | Max. Allowable Asym. for Ch 1 (ms) | Port 87 | Differential |  |  | FALSE | P87 | FALSE
87CHTRG | 87CH1AL OR 87LSP OR R_TRIG 87BLKL OR R_TRIG 87BLK OR 87OP | 87L Recording Trigger Equation (SELogic) | Port 87 | Event |  |  | FALSE | P87 | FALSE
87CH1PC | OFF | Ch 1 Lost Packet Alarm Threshold | Port 87 | Enable |  |  | FALSE | P87 | FALSE
87R11PU | 4 | Received Bit 1, Port 1 Pickup Time (ms) | Port 87 | Differential |  |  | FALSE | P87 | FALSE
87R11DO | 4 | Received Bit 1, Port 1 Dropout Time (ms) | Port 87 | Differential |  |  | FALSE | P87 | FALSE
87R21PU | 4 | Received Bit 2, Port 1 Pickup Time (ms) | Port 87 | Differential |  |  | FALSE | P87 | FALSE
87R21DO | 4 | Received Bit 2, Port 1 Dropout Time (ms) | Port 87 | Differential |  |  | FALSE | P87 | FALSE
87R31PU | 4 | Received Bit 3, Port 1 Pickup Time (ms) | Port 87 | Differential |  |  | FALSE | P87 | FALSE
87R31DO | 4 | Received Bit 3, Port 1 Dropout Time (ms) | Port 87 | Differential |  |  | FALSE | P87 | FALSE
87R41PU | 4 | Received Bit 4, Port 1 Pickup Time (ms) | Port 87 | Differential |  |  | FALSE | P87 | FALSE
87R41DO | 4 | Received Bit 4, Port 1 Dropout Time (ms) | Port 87 | Differential |  |  | FALSE | P87 | FALSE
CTRW | 400 | Current Transformer Ratio - Input W | Line Configuration | Ratio |  |  | FALSE | S1 | FALSE
CTRX | 400 | Current Transformer Ratio - Input X | Line Configuration | Ratio |  |  | FALSE | S1 | FALSE
PTRY | 1200.0 | Potential Transformer Ratio - Input Y | Line Configuration | Ratio |  |  | FALSE | S1 | FALSE
PTRZ | 1200.0 | Potential Transformer Ratio - Input Z | Line Configuration | Ratio |  |  | FALSE | S1 | FALSE
Z1MAG | 2.02 | Positive-Sequence Line Impedance Magnitude (ohms,sec) | Line Configuration | Line Impedance |  |  | FALSE | S1 | FALSE
Z1ANG | 80.95 | Positive-Sequence Line Impedance Angle (deg) | Line Configuration | Line Impedance |  |  | FALSE | S1 | FALSE
Z0MAG | 4.97 | Zero-Sequence Line Impedance Magnitude (ohms,sec) | Line Configuration | Line Impedance |  |  | FALSE | S1 | FALSE
Z0ANG | 82.17 | Zero-Sequence Line Impedance Angle (deg) | Line Configuration | Line Impedance |  |  | FALSE | S1 | FALSE
E87L | Y | Enable Line Current Differential Protection 87L | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
E87OCTL | Y | Enable Open CT Detection Logic | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
E21MP | 2 | Enable Mho Phase Distance Zones | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
E21XP | N | Enable Quadrilateral Phase Distance Zones | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
E21MG | N | Enable Mho Ground Distance Zones | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
E21XG | 2 | Enable Quadrilateral Ground Distance Zones | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
ECVT | Y | Enable CVT Transient Detection | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
ECDTD | Y | Enable Distance Element Common Time Delay | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
ESOTF | N | Enable Switch-Onto-Fault | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
ELOAD | N | Enable Load Encroachment | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
E50P | N | Enable Phase Instantaneous/Definite-Time Overcurrent Elements | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
E51 | 1 | Enable Inverse Time Overcurrent Elements | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
E32 | Y | Enable Directional Control | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
E79 | N | Enable Reclosing | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
EMANCL | N | Enable Manual Closing | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
EADVS | Y | Enable Advanced Settings | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
EFID | N | Enable FID Logic | Relay Configuration | Enable |  |  | FALSE | S1 | FALSE
87CTXL | 0 | Condition for which Terminal X is included in 87L Element Equation (SELogic) | 87 Current Differential | Differential Settings |  |  | FALSE | S1 | FALSE
87CTP1R | 2000 | Maximum Primary Current Rating for Remote Relay 1 CT | 87 Current Differential | Differential Settings |  |  | FALSE | S1 | FALSE
ESTUB | NOT IN202 | Condition for which Stub protection is enabled Equation (SELogic) | 87 Current Differential | Differential Settings |  |  | FALSE | S1 | FALSE
87BLOCK | PLT01 OR PSV03 | Conditions for Blocking Line Differential protection Equation (SELogic) | 87 Current Differential | Differential Settings |  |  | FALSE | S1 | FALSE
87LPP | 0.10 | Pickup value for Phase Differential Element (p.u.) | 87 Current Differential | Phase Diff Settings |  |  | FALSE | S1 | FALSE
87LPPS | 0.12 | Secure Mode Pickup value for Phase Differential Element (p.u.) | 87 Current Differential | Phase Diff Settings |  |  | FALSE | S1 | FALSE
87LQP | OFF | Pickup value for Negative Sequence Differential Element (p.u.) | 87 Current Differential | Negative Seq. Dif Settings |  |  | FALSE | S1 | FALSE
87LQPS | OFF | Secure Mode Pickup value for Negative Sequence Differential Element (p.u.) | 87 Current Differential | Negative Seq. Dif Settings |  |  | FALSE | S1 | FALSE
87LGP | 0.20 | Pickup value for Zero Sequence Differential Element (p.u.) | 87 Current Differential | Ground Differential Settings |  |  | FALSE | S1 | FALSE
87LGPS | 0.24 | Secure Mode Pickup value for Zero Sequence Differential Element (p.u.) | 87 Current Differential | Ground Differential Settings |  |  | FALSE | S1 | FALSE
RSTOCT | 87ROCT | Reset Condition for Open CT detection logic Equation (SELogic) | 87 Open CT Detection Logic | Reset |  |  | TRUE | S1 | FALSE
Z1MP | 1.72 | Zone 1 Reach (ohms,sec) | Mho Phase Distance Reach | Mho Phase Distance |  |  | TRUE | S1 | FALSE
Z2MP | 2.53 | Zone 2 Reach (ohms,sec) | Mho Phase Distance Reach | Mho Phase Distance |  |  | TRUE | S1 | FALSE
Z1PD | 0 | Zone 1 Time Delay (cyc) | Phase Distance Time Delay | Phase Distance |  |  | TRUE | S1 | FALSE
Z2PD | OFF | Zone 2 Time Delay (cyc) | Phase Distance Time Delay | Phase Distance |  |  | FALSE | S1 | FALSE
Z3PD | OFF | Zone 3 Time Delay (cyc) | Phase Distance Time Delay | Phase Distance |  |  | TRUE | S1 | FALSE
ARESE | N | Enable Adaptive Resistive Element (Y, N) | Quad Ground Distance Reach | Quad Ground Distance |  |  | TRUE | S1 | FALSE
XG1 | 1.62 | Zone 1 Reactance (ohms,sec) | Quad Ground Distance Reach | Quad Ground Distance |  |  | TRUE | S1 | FALSE
RG1 | 3.00 | Zone 1 Resistance (ohms,sec) | Quad Ground Distance Reach | Quad Ground Distance |  |  | FALSE | S1 | FALSE
XG2 | 2.53 | Zone 2 Reactance (ohms,sec) | Quad Ground Distance Reach | Quad Ground Distance |  |  | TRUE | S1 | FALSE
RG2 | 5.00 | Zone 2 Resistance (ohms,sec) | Quad Ground Distance Reach | Quad Ground Distance |  |  | TRUE | S1 | FALSE
XGPOL | IG | Quad Ground Polarizing Quantity | Quad Ground Distance Reach | Quad Ground Distance |  |  | FALSE | S1 | FALSE
TANGG | 0.0 | Ground Nonhomogeneous Correction Angle (deg) | Quad Ground Distance Reach | Quad Ground Distance |  |  | TRUE | S1 | FALSE
Z1XGTC | 1 | Quad Ground Zone 1 Torque Control | Quad Ground Distance Reach | Quad Ground Distance |  |  | FALSE |  | FALSE
Z2XGTC | 1 | Quad Ground Zone 2 Torque Control | Quad Ground Distance Reach | Quad Ground Distance |  |  | FALSE |  | FALSE
k0M1 | 0.485 | Zone 1 ZSC Factor Magnitude | Zero-Sequence Compensation Factor | Zero-Sequence Compensation |  |  | FALSE | S1 | FALSE
k0A1 | 2.05 | Zone 1 ZSC Factor Angle (deg) | Zero-Sequence Compensation Factor | Zero-Sequence Compensation |  |  | TRUE | S1 | FALSE
k0M | 0.485 | Forward Zones ZSC Factor Magnitude | Zero-Sequence Compensation Factor | Zero-Sequence Compensation |  |  | FALSE | S1 | FALSE
k0A | 2.05 | Forward Zones ZSC Factor Angle (deg) | Zero-Sequence Compensation Factor | Zero-Sequence Compensation |  |  | TRUE | S1 | FALSE
k0MR | 0.485 | Reverse Zones ZSC Factor Magnitude | Zero-Sequence Compensation Factor | Zero-Sequence Compensation |  |  | FALSE | S1 | FALSE
k0AR | 2.05 | Reverse Zones ZSC Factor Angle (deg) | Zero-Sequence Compensation Factor | Zero-Sequence Compensation |  |  | TRUE | S1 | FALSE
Z1GD | 0 | Zone 1 Time Delay (cyc) | Ground Distance Time Delay | Ground Distance |  |  | FALSE |  | FALSE
Z2GD | OFF | Zone 2 Time Delay (cyc) | Ground Distance Time Delay | Ground Distance |  |  | FALSE | S1 | FALSE
Z3GD | OFF | Zone 3 Time Delay (cyc) | Ground Distance Time Delay | Ground Distance |  |  | TRUE | S1 | FALSE
Z1D | 0 | Zone 1 Time Delay (cyc) | Distance Time Delay | Common Distance |  |  | FALSE |  | FALSE
Z2D | 42.000 | Zone 2 Time Delay (cyc) | Distance Time Delay | Common Distance |  |  | TRUE | S1 | FALSE
Z3D | OFF | Zone 3 Time Delay (cyc) | Distance Time Delay | Common Distance |  |  | TRUE | S1 | FALSE
51O01 | LIGFIM | Inverse Time Overcurrent 01 Operate Quantity | Inverse TOC | Overcurrent Protection |  |  | FALSE | S1 | FALSE
51P01 | 1.200000 | Inverse Time Overcurrent 01 Pickup Value Equation (SELogic) | Inverse TOC | Overcurrent Protection |  |  | TRUE | S1 | FALSE
51C01 | U2 | Inverse Time Overcurrent 01 Curve Selection | Inverse TOC | Overcurrent Protection |  |  | FALSE | S1 | TRUE
51TD01 | 2.000000 | Inverse Time Overcurrent 01 Time Dial Equation (SELogic) | Inverse TOC | Overcurrent Protection |  |  | FALSE | S1 | TRUE
51TC01 | 32GF | Inverse Time Overcurrent 01 Torque Control Equation (SELogic) | Inverse TOC | Overcurrent Protection |  |  | FALSE | S1 | TRUE
50FP | 0.30 | Forward Directional Overcurrent Pickup (A,sec) | Directional Control Element | Directional Protection |  |  | FALSE | S1 | TRUE
a2 | 0.03 | Positive-Sequence Restraint Factor, I2/I1 | Directional Control Element | Directional Protection |  |  | FALSE | S1 | TRUE
k2 | 0.10 | Zero-Sequence Restraint Factor, I2/I0 | Directional Control Element | Directional Protection |  |  | FALSE | S1 | FALSE
LLR | 8.14 | Line Length | Fault Locator | General Protection |  |  | FALSE | S1 | FALSE
TR | (87OP AND NOT 87LST) OR Z1P OR Z1G OR Z2T OR 51T01 | Trip Equation (SELogic) | Trip Logic | Trip |  |  | FALSE | S1 | TRUE
DTA | PSV02 AND NOT PLT03 | Direct Transfer Trip A-Phase Equation (SELogic) | Trip Logic | Trip |  |  | FALSE | S1 | TRUE
DTB | PSV02 AND NOT PLT03 | Direct Transfer Trip B-Phase Equation (SELogic) | Trip Logic | Trip |  |  | FALSE | S1 | FALSE
DTC | PSV02 AND NOT PLT03 | Direct Transfer Trip C-Phase Equation (SELogic) | Trip Logic | Trip |  |  | FALSE | S1 | FALSE
BK1MTR | NA | Breaker 1 Manual Trip Equation (SELogic) | Trip Logic | Trip |  |  | FALSE | S1 | FALSE
ULTR | TRGTR | Unlatch Trip Equation (SELogic) | Trip Logic | Trip |  |  | FALSE |  | FALSE
ULMTR1 | 1 | Unlatch Manual Trip -BK1 Equation (SELogic) | Trip Logic | Trip |  |  | FALSE | S1 | FALSE
TOPD | 5.000 | Trip During Open Pole Time Delay (cyc) | Trip Logic | Trip |  |  | FALSE | S1 | FALSE
TULO | 1 | Trip Unlatch Option | Trip Logic | Trip |  |  | FALSE | S1 | FALSE
TDUR3D | 9.000 | 3PT Minimum Trip Duration Time Delay (cyc) | Trip Logic | Trip |  |  | FALSE | S1 | FALSE
ER | R_TRIG Z2P OR R_TRIG Z2G OR R_TRIG PSV01 OR R_TRIG PSV02 OR R_TRIG 3PT OR R_TRIG 87BLK OR R_TRIG 87LST OR R_TRIG IN205 OR R_TRIG 51S01 OR R_TRIG PCT02Q | Event Report Trigger Equation (SELogic) | Trip Logic | Event |  |  | FALSE | S1 | FALSE
PROTSEL1 | # PB1 IS FOR LOCAL 87L BLOCK CONTROL | Local 87L Block | Protection Logic | Block |  |  | FALSE | L1 | FALSE
PROTSEL2 | PLT01S := PB1_PUL AND NOT PLT01 # 87L BLOCK | Local 87L Block (Set) | Protection Logic | Block |  |  | FALSE | L1 | FALSE
PROTSEL3 | PLT01R := PB1_PUL AND PLT01 | Local 87L Block (Reset) | Protection Logic | Block |  |  | FALSE | L1 | FALSE
PROTSEL4 |  |  | Protection Logic |  |  |  | FALSE | L1 | TRUE
PROTSEL5 | # PB2 IS FOR DTT SENT BLOCK/UNBLOCK CONTROL | DTT Transmit Block | Protection Logic | Block |  |  | FALSE | L1 | FALSE
PROTSEL6 | PLT02S := PB2_PUL AND NOT PLT02 | DTT Transmit Block (Set) | Protection Logic | Block |  |  | FALSE | L1 | TRUE
PROTSEL7 | PLT02R := PB2_PUL AND PLT02 | DTT Transmit Block (Reset) | Protection Logic | Block |  |  | FALSE | L1 | FALSE
PROTSEL8 |  |  | Protection Logic |  |  |  | FALSE | L1 | TRUE
PROTSEL9 | #PB3 IS TO BLOCK/UNBLOCKE RECEIVED DTT | DTT Receive Block | Protection Logic | Block |  |  | FALSE | L1 | FALSE
PROTSEL10 | PLT03S := PB3_PUL AND NOT PLT03 | DTT Receive Block (Set) | Protection Logic | Block |  |  | FALSE | L1 | TRUE
PROTSEL11 | PLT03R := PB3_PUL AND PLT03 | DTT Receive Block (Reset) | Protection Logic | Block |  |  | FALSE | L1 | FALSE
PROTSEL12 |  |  | Protection Logic |  |  |  | FALSE | L1 | TRUE
PROTSEL13 | # PB4 IS TO ENABLE/DISABLE 87L TEST MODE | 87L Test Mode Enable | Protection Logic | Enable |  |  | FALSE | L1 | FALSE
PROTSEL14 | PLT04S := PB4_PUL AND NOT PLT04 | 87L Test Mode Enable (Set) | Protection Logic | Enable |  |  | FALSE | L1 | TRUE
PROTSEL15 | PLT04R := PB4_PUL AND PLT04 | 87L Test Mode Enable (Reset) | Protection Logic | Enable |  |  | FALSE | L1 | FALSE
PROTSEL16 |  |  | Protection Logic |  |  |  | FALSE | L1 | TRUE
PROTSEL17 | PSV01 := NOT PLT02 AND IN205 AND IN202 | DTT Transmit Status | Protection Logic | Indication |  |  | FALSE | L1 | FALSE
PROTSEL18 | PSV02 := 87CH1OK AND 87R01P1 | DTT Receive Status | Protection Logic | Indication |  |  | FALSE | L1 | FALSE
PROTSEL19 | PSV03 := 87CH1OK AND 87R06P1 | Remote 87 Block Status | Protection Logic | Indication |  |  | FALSE | L1 | FALSE
PROTSEL20 | PSV04 := 87CH1OK AND 87R07P1 | Remote Breaker Status (b) | Protection Logic | Indication |  |  | FALSE | L1 | FALSE
PROTSEL21 | PSV05 := 87CH1OK AND NOT 87R07P1 | Remote Breaker Status (a) | Protection Logic | Indication |  |  | FALSE | L1 | FALSE
PROTSEL22 |  |  | Protection Logic |  |  |  | FALSE | L1 | FALSE
PROTSEL23 | # DTT RX INDICATION | DTT Received Indication | Protection Logic | Indication |  |  | FALSE | L1 | FALSE
PROTSEL24 | PLT05S := PSV02 AND NOT PLT05 | DTT Received Indication (Set) | Protection Logic | Indication |  |  | FALSE | L1 | FALSE
PROTSEL25 | PLT05R := NOT PSV02 AND TRGTR AND PLT05 | DTT Received Indication (Reset) | Protection Logic | Indication |  |  | FALSE | L1 | FALSE
PROTSEL26 |  |  | Protection Logic |  |  |  | FALSE | L1 | FALSE
PROTSEL27 | # DTT TX INDICATION | DTT Transmitted Indication | Protection Logic | Indication |  |  | FALSE | L1 | FALSE
PROTSEL28 | PLT06S := PSV01 AND NOT PLT06 | DTT Transmitted Indication (Set) | Protection Logic | Indication |  |  | FALSE | L1 | FALSE
PROTSEL29 | PLT06R := NOT PSV01 AND TRGTR AND PLT06 | DTT Transmitted Indication (Reset) | Protection Logic | Indication |  |  | FALSE | L1 | FALSE
PROTSEL30 |  |  | Protection Logic |  |  |  | FALSE | L1 | FALSE
PROTSEL31 | PCT01IN := LOP # FOR LOP ALARM | Loss of Potential Alarm | Protection Logic | Indication |  |  | FALSE | L1 | FALSE
PROTSEL32 | PCT01PU := 600.000000 | Loss of Potential Alarm Pickup | Protection Logic | Indication |  |  | FALSE | L1 | FALSE
PROTSEL33 | PCT01DO := 1.000000 | Loss of Potential Alarm Dropout | Protection Logic | Indication |  |  | FALSE | L1 | FALSE
PROTSEL34 |  |  | Protection Logic |  |  |  | FALSE | L1 | FALSE
PROTSEL35 | #PB12 USED FOR MANUAL RELAY EVENT/RECORD TRIGGER, PRESS PB12 FOR 1S | Manual Event Report Trigger | Protection Logic | Event |  |  | FALSE | L1 | FALSE
PROTSEL36 | PCT02IN := PB12 | Manual Event Report Trigger | Protection Logic | Event |  |  | FALSE | L1 | FALSE
PROTSEL37 | PCT02PU := 60.000000 | Manual Event Report Trigger | Protection Logic | Event |  |  | FALSE | L1 | FALSE
PROTSEL38 | PCT02DO := 30.000000 | Manual Event Report Trigger | Protection Logic | Event |  |  | FALSE | L1 | FALSE
OUT201 | 3PT #THREE POLE TRIP | Interface Board 1 Output OUT201 (SELogic) | Interface Board Outputs | Trip |  |  | FALSE | O1 | FALSE
OUT202 | PCT01Q | Interface Board 1 Output OUT202 (SELogic) | Interface Board Outputs | LOP Alarm (Not Wired) |  |  | FALSE | O1 | FALSE
OUT203 | PSV02 AND NOT PLT03 | Interface Board 1 Output OUT203 (SELogic) | Interface Board Outputs | 86DTT Trip |  |  | FALSE | O1 | FALSE
OUT204 | 3PT #BFI | Interface Board 1 Output OUT204 (SELogic) | Interface Board Outputs | Breaker Failure |  |  | FALSE | O1 | FALSE
OUT206 | NA | Interface Board 1 Output OUT206 (SELogic) | Interface Board Outputs | Inactive |  |  | FALSE | O1 | FALSE
OUT207 | NA | Interface Board 1 Output OUT207 (SELogic) | Interface Board Outputs | Inactive |  |  | FALSE | O1 | FALSE
OUT208 | NA | Interface Board 1 Output OUT208 (SELogic) | Interface Board Outputs | Inactive |  |  | FALSE | O1 | FALSE
OUT214 | NOT (SALARM OR HALARM) | Interface Board 1 Output OUT214 (SELogic) | Interface Board Outputs | Alarm |  |  | FALSE | O1 | FALSE
OUT303 | 3PT #RELAY TRIP TO DFR | Interface Board 2 Output OUT303 (SELogic) | Interface Board Outputs | Alarm |  |  | FALSE | O1 | FALSE
87T1P1 | PSV01 | Serial Comm. Transmit Bit 1 Port 1 (SELogic) | 87L Communication Bits | Remote 86DTT Trip |  |  | FALSE | O1 | FALSE
87T6P1 | PLT01 | Serial Comm. Transmit Bit 6 Port 1 (SELogic) | 87L Communication Bits | Local 87L Disable |  |  | FALSE | O1 | FALSE
87T7P1 | NOT IN201 OR NOT IN202 | Serial Comm. Transmit Bit 7 Port 1 (SELogic) | 87L Communication Bits | Local Terminal Open |  |  | FALSE | O1 | FALSE
PB1_LED | PLT01 #87L BLOCKED LOCALLY | Pushbutton LED 1 (SELogic) | Pushbuttons | Block |  |  | FALSE | F1 | FALSE
PB1_COL | RO | PB1_LED Assert && Deassert Color | Pushbuttons | Block |  |  | FALSE | F1 | FALSE
PB2_LED | PLT02 #BF DTT TX BLOCKED | Pushbutton LED 2 (SELogic) | Pushbuttons | Block |  |  | FALSE | F1 | FALSE
PB2_COL | RO | PB2_LED Assert && Deassert Color | Pushbuttons | Block |  |  | FALSE | F1 | FALSE
PB3_LED | PLT03 #BF DTT RX BLOCKED | Pushbutton LED 3 (SELogic) | Pushbuttons | Block |  |  | FALSE | F1 | FALSE
PB3_COL | RO | PB3_LED Assert && Deassert Color | Pushbuttons | Block |  |  | FALSE | F1 | FALSE
PB4_LED | PLT04 #87L TEST MODE ENABLED | Pushbutton LED 4 (SELogic) | Pushbuttons | Enable |  |  | FALSE | F1 | FALSE
PB4_COL | RO | PB4_LED Assert && Deassert Color | Pushbuttons | Enable |  |  | FALSE | F1 | FALSE
PB5_LED | PLT05 #DTT SIGNAL RECEIVED | Pushbutton LED 5 (SELogic) | Pushbuttons | Indication |  |  | FALSE | F1 | FALSE
PB5_COL | RO | PB5_LED Assert && Deassert Color | Pushbuttons | Indication |  |  | FALSE | F1 | FALSE
PB6_LED | PLT06 #DTT SIGNAL SENT | Pushbutton LED 6 (SELogic) | Pushbuttons | Indication |  |  | FALSE | F1 | FALSE
PB6_COL | RO | PB6_LED Assert && Deassert Color | Pushbuttons | Indication |  |  | FALSE | F1 | FALSE
PB7_LED | IN201 #BKR CLOSED | Pushbutton LED 7 (SELogic) | Pushbuttons | Indication |  |  | FALSE | F1 | FALSE
PB7_COL | RG | PB7_LED Assert && Deassert Color | Pushbuttons | Indication |  |  | FALSE | F1 | FALSE
PB8_LED | IN202 #LSW CLOSED | Pushbutton LED 8 (SELogic) | Pushbuttons | Indication |  |  | FALSE | F1 | FALSE
PB8_COL | RG | PB8_LED Assert && Deassert Color | Pushbuttons | Indication |  |  | FALSE | F1 | FALSE
PB9_LED | PSV03 #87L BLOCKED REMOTELY | Pushbutton LED 9 (SELogic) | Pushbuttons | Indication |  |  | FALSE | F1 | FALSE
PB9_COL | RO | PB9_LED Assert && Deassert Color | Pushbuttons | Indication |  |  | FALSE | F1 | FALSE
PB10LED | PSV05 #REMOTE TERMINAL CLOSED | Pushbutton LED 10 (SELogic) | Pushbuttons | Indication |  |  | FALSE | F1 | FALSE
PB10COL | RO | PB10LED Assert && Deassert Color | Pushbuttons | Indication |  |  | FALSE | F1 | FALSE
PB11LED | PSV04 #REMOTE TERMINAL OPEN | Pushbutton LED 11 (SELogic) | Pushbuttons | Indication |  |  | FALSE | F1 | FALSE
PB11COL | GO | PB11LED Assert && Deassert Color | Pushbuttons | Indication |  |  | FALSE | F1 | FALSE
PB12LED | PCT02Q #MANUAL RELAY TRIGGER | Pushbutton LED 12 (SELogic) | Pushbuttons | Event |  |  | FALSE | F1 | FALSE
PB12COL | RO | PB12LED Assert && Deassert Color | Pushbuttons | Event |  |  | FALSE | F1 | FALSE
T2_LED | Z2T OR 51T01 | Target LED 2 (SELogic) | Target LEDs | Indication |  |  | FALSE | F1 | FALSE
T6_LED | (Z2P OR Z2G) AND NOT (TLED_6 OR TLED_7 OR TLED_8) | Target LED 6 (SELogic) | Target LEDs | Indication |  |  | FALSE | F1 | FALSE
T6LEDL | N | Target LED 6 Latch | Target LEDs | Indication |  |  | FALSE | F1 | FALSE
T7_LED | (Z3P OR Z3G) AND NOT (TLED_5 OR TLED_6 OR TLED_8) | Target LED 7 (SELogic) | Target LEDs | Indication |  |  | FALSE | F1 | FALSE
T7LEDL | N | Target LED 7 Latch | Target LEDs | Indication |  |  | FALSE | F1 | FALSE
T8LEDL | N | Target LED 8 Latch | Target LEDs | Indication |  |  | FALSE | F1 | FALSE
T16_LED | IN203 | Target LED 16 (SELogic) | Target LEDs | Indication |  |  | FALSE | F1 | FALSE
T17LEDC | GO | T17_LED Assert && Deassert Color | Target LEDs | Indication |  |  | FALSE | F1 | FALSE
T19_LED | BK1LO | Target LED 19 (SELogic) | Target LEDs | Indication |  |  | FALSE | F1 | FALSE
T21LEDL | N | Target LED 21 Latch | Target LEDs | Indication |  |  | FALSE | F1 | TRUE
RMS_V | Y | RMS Line Voltage Screen | Selectable Screens | Relay Configuration |  |  | FALSE | F1 | FALSE
RMS_W | Y | RMS Active Power Screen | Selectable Screens | Relay Configuration |  |  | FALSE | F1 | FALSE
FUNDVAR | Y | Fundamental Reactive Power Screen | Selectable Screens | Relay Configuration |  |  | FALSE | F1 | FALSE
RMS_VA | Y | RMS Apparent Power Screen | Selectable Screens | Relay Configuration |  |  | FALSE | F1 | FALSE
STA_BAT | Y | Station Battery Screen | Selectable Screens | Relay Configuration |  |  | FALSE | F1 | FALSE
FUND_VI | N | Fundamental Voltage and Current Screen | Selectable Screens | Relay Configuration |  |  | FALSE | F1 | TRUE
ONELINE | N | One Line Bay Control Diagram | Selectable Screens | Relay Configuration |  |  | FALSE | F1 | FALSE
SER_PP | Y | 5 Events per SER Events page? (Y for 5, N for 3) | SER Parameters | SER |  |  | FALSE | F1 | FALSE
SRDLCNT | 5 | Number of Counts Before Auto-Removal | SER Chatter Criteria | SER |  |  | FALSE | R1 | FALSE
SRDLTIM | 1.0 | Time for Auto-Removal (seconds) | SER Chatter Criteria | SER |  |  | FALSE | R1 | FALSE
SITM1 | IN201,"BKR 52T1",CLOSED,OPENED,N | SER Points and Aliases, Point 1 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM2 | IN202,"SW 89L1",CLOSED,OPENED,N | SER Points and Aliases, Point 2 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM3 | PLT01,"Local 87L",Blocked,Enabled,N | SER Points and Aliases, Point 3 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM4 | PSV03,"Remote 87L",Blocked,Enabled,N | SER Points and Aliases, Point 4 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM5 | 87DD,"87 Disturbance",Detected,OFF,N | SER Points and Aliases, Point 5 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM6 | 87DDR,"Remote 87L disturb",Detected,Drop-out,N | SER Points and Aliases, Point 6 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM7 | 87BLK,"87L Function",Blocked,Enabled,N | SER Points and Aliases, Point 7 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM8 | 87CH1AL,"87 COMM CH1",Alarm,OK,N | SER Points and Aliases, Point 8 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM9 | 87OCTA,"PH-A Open CT",Detected,Reset,N | SER Points and Aliases, Point 9 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM10 | 87OCTB,"PH-B Open CT",Detected,Reset,N | SER Points and Aliases, Point 10 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM11 | 87OCTC,"PH-C Open CT",Detected,Reset,N | SER Points and Aliases, Point 11 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM12 | PHASE_A,"PH-A FLT",Detected,Reset,N | SER Points and Aliases, Point 12 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM13 | PHASE_B,"PH-B FLT",Detected,Reset,N | SER Points and Aliases, Point 13 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM14 | PHASE_C,"PH-C FLT",Detected,Reset,N | SER Points and Aliases, Point 14 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM15 | TLED_12,"GND FLT",Detected,Reset,N | SER Points and Aliases, Point 15 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM16 | 87LA,"87L A phase",Operate,Reset,N | SER Points and Aliases, Point 16 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM17 | 87LB,"87L B phase",Operate,Reset,N | SER Points and Aliases, Point 17 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM18 | 87LC,"87L C phase",Operate,Reset,N | SER Points and Aliases, Point 18 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM19 | 87LQ,87-3I2,Operate,Reset,N | SER Points and Aliases, Point 19 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM20 | 87LG,87-IG,Operate,Reset,N | SER Points and Aliases, Point 20 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM21 | Z1P,Z1P,Trip,Reset,N | SER Points and Aliases, Point 21 | SER Points and Aliases | SER |  |  | FALSE | R1 | FALSE
SITM22 | Z1G,Z1G,Trip,Reset,N | SER Points and Aliases, Point 22 | SER Points and Aliases | SER |  |  | TRUE | R1 | FALSE
SITM23 | PLT02,"DTT Sent",Blocked,Enabled,N | SER Points and Aliases, Point 23 | SER Points and Aliases | SER |  |  | TRUE | R1 | FALSE
SITM24 | PLT03,"Received DTT trip",Disabled,Enabled,N | SER Points and Aliases, Point 24 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM25 | PLT04,"87L Test mode",Enabled,Disabled,N | SER Points and Aliases, Point 25 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM26 | 87R01P1,"DTT over 87CH1",Received,Reset,N | SER Points and Aliases, Point 26 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM27 | 87R06P1,"Remote 87L",Blocked,Unblock,N | SER Points and Aliases, Point 27 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM28 | 87R07P1,"Remote Open Status",Received,Dropout,N | SER Points and Aliases, Point 28 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM29 | 87T1P1,"DTT over 87CH1",Sent,Reset,N | SER Points and Aliases, Point 29 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM30 | 87T6P1,"Local 87L block",Sent,Reset,N | SER Points and Aliases, Point 30 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM31 | 87T7P1,"WD PWR TMN Open",Assert,De-assert,N | SER Points and Aliases, Point 31 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM32 | IN203,"DTT Lockout relay",Operate,Reset,N | SER Points and Aliases, Point 32 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM33 | IN205,"BF DTT Trip input",Assert,De-assert,N | SER Points and Aliases, Point 33 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM34 | Z2P,Z2P,Pick-up,Reset,N | SER Points and Aliases, Point 34 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM35 | Z2G,Z2G,Pick-up,Reset,N | SER Points and Aliases, Point 35 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM36 | Z2T,"ZONE 2 ELEMENT",Trip,Reset,N | SER Points and Aliases, Point 36 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM37 | 51S01,"Timed GND DOC",Picked-up,Reset,N | SER Points and Aliases, Point 37 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM38 | 51T01,"Timed GND DOC trip",Operated,Reset,N | SER Points and Aliases, Point 38 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM39 | PCT01Q,"LOP ALARM",Present,Reset,N | SER Points and Aliases, Point 39 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM40 | OUT201,"OUT201 - Trip",Close,Open,N | SER Points and Aliases, Point 40 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM41 | OUT203,"OUT203 - DTT Rx",Close,Open,N | SER Points and Aliases, Point 41 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM42 | OUT204,"OUT204 - BFI",Close,Open,N | SER Points and Aliases, Point 42 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SITM43 | OUT303,"OUT303 to DFR",Close,Open,N | SER Points and Aliases, Point 43 | SER Points and Aliases | SER |  |  | FALSE | R1 | TRUE
SPAQ | VARMS,VBRMS,VCRMS,LIARMS,LIBRMS,LICRMS,87IAFM,87IBFM,87ICFM,87I1FM,87IGFM,87IQFM,FLOC,87LOC,DC1,87KA,87KB,87KC,87KQ,87KG | SPAQ | Signal Profile Analog Quantities | SER |  |  | FALSE | R1 | TRUE
SPEN | NOT 3PO | Signal Profile Enable (SELogic) | Signal Profile | Enable |  |  | FALSE | R1 | TRUE
ERDIG | S | Store Selected (S) or All (A) Relay Word Bits | Event Reporting | Event |  |  | FALSE | R1 | TRUE
SRATE | 8 | Sample Rate of Event Report (kHz) | Event Reporting | Event |  |  | FALSE | R1 | TRUE
LER | 1.00 | Length of Event Report (seconds) | Event Reporting | Event |  |  | FALSE | R1 | TRUE
PRE | 0.35 | Length of Pre-Fault (seconds) | Event Reporting | Event |  |  | FALSE | R1 | TRUE
ERAQ | IAWFM,IAWFA,IBWFM,IBWFA,ICWFM,ICWFA,VAYFM,VAYFA,VBYFM,VBYFA,VCYFM,VCYFA,87IAFM,87IBFM,87ICFM,RLYTEMP,87CH1RT,87CH1AX | ERAQ | Event Reporting Analog Quantities | Event |  |  | FALSE | R1 | TRUE
ERDG | 87LA,87LB,87LC,87LQ,87LG,#,TRIP,COMPRM,#,Z1P,Z2P,Z3P,#,Z1PT,Z2PT,Z3PT,#,Z1G,Z2G,Z3G,#,Z2T,Z1GT,Z2GT,Z3GT,#,VPOLV,ZLOAD,LOP,#,OSB,OST,#,3PO,#,32QF,F32P,32QR,32GF,32GR,F32V,R32V,32VE,F32QG,R32QG,#,67G1,#,PT,KEY,Z3RB,#,PSV01,PSV02,PSV03,PSV04,PSV05,#,PLT01,PLT02,PLT03,PLT04,PLT05,PLT06,#,PCT01Q,PCT02Q,PCT03Q,PCT04Q,PCT05Q,#,87C1BCH,87C2BCH,87C3BCH,87HSB,#,IN201,IN202,IN203,IN204,IN205,IN206,IN207,IN301,IN302,#,87USAFE,ESTUB,87DD,87LST,87BLK,87BLKL,87OCT,87CH1AL,87DTTRX,#,OUT201,OUT202,OUT203,OUT204,OUT205,OUT206,OUT303,#,51S01,51T01,#,67G2,67G3,#,87R01P1,87R02P1,87R03P1,87R04P1,87R05P1,87R06P1,87R07P1,87R08P1,#,87T1P1,87T2P1,87T3P1,87T5P1,87T6P1,87T7P1,87T8P1,#,PB1_PUL,PB2_PUL,PB3_PUL,PB4_PUL,PB12 | ERDG | Event Reporting Digital Quantities | Event |  |  | FALSE | R1 | TRUE
EPORT | Y | Enable Port | Communications | Port F |  |  | FALSE | PF | FALSE
PROTO | SEL | Protocol | Communications | Port F |  |  | FALSE | PF | FALSE
SPEED | 19200 | Baud Rate | Communications | Port F |  |  | FALSE | PF | FALSE
EPORT | Y | Enable Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DEFRTR | 172.31.100.254 | Default Router | Communications | Port 5 |  |  | FALSE | P5 | FALSE
NETMODE | FAILOVER | Operating Mode | Communications | Port 5 |  |  | FALSE | P5 | FALSE
NETPORT | A | Primary Network Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ETELNET | Y | Enable Telnet | Communications | Port 5 |  |  | FALSE | P5 | FALSE
TPORT | 23 | Telnet Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
EDNP | 1 | Enable DNP Sessions | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPADR | 1 | DNP Address | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPPNUM | 20000 | DNP TCP Port | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPIP1 | 172.31.100.241 | DNP Client IP | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPTR1 | TCP | DNP Transport Protocol | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DNPMAP1 | 1 | DNP Session Map | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLA1 | 0 | Currents Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECVPLV1 | 0 | Voltages Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
DECPLM1 | 0 | Misc Scaling Decimal Places | Communications | Port 5 |  |  | FALSE | P5 | FALSE
AIVAR1 | 5 | Default Analog Input Variation | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBA1 | 0 | Deadband, Currents | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBV1 | 0 | Deadband, Voltages | Communications | Port 5 |  |  | FALSE | P5 | FALSE
ANADBM1 | 0 | Deadband, Misc | Communications | Port 5 |  |  | FALSE | P5 | FALSE
MINDIST | OFF | Min Fault Location to Capture | Communications | Port 5 |  |  | FALSE | P5 | FALSE
MAXDIST | OFF | Max Fault Location to Capture | Communications | Port 5 |  |  | FALSE | P5 | FALSE
BI_1 | RLY_EN | Relay Enabled | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_2 | IN201 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_3 | IN202 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_4 | IN203 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_5 | IN205 | IO | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_6 | TLED_1 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_7 | TLED_2 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_8 | TLED_3 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_9 | TLED_4 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_10 | TLED_5 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_11 | TLED_6 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_12 | TLED_7 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_13 | TLED_8 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_14 | TLED_9 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_15 | TLED_10 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_16 | TLED_11 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_17 | TLED_12 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_18 | TLED_13 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_19 | TLED_14 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_20 | TLED_15 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_21 | TLED_16 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_22 | TLED_21 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_23 | TLED_22 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_24 | TLED_23 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_25 | TLED_24 | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_26 | TRIPLED | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_27 | PB1_LED | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_28 | PB2_LED | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_29 | PB3_LED | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_30 | PB4_LED | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_31 | PB5_LED | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_32 | PB6_LED | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_33 | PB9_LED | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_34 | PB10LED | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BI_35 | PB11LED | LEDs | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_1 | LIAFM | Current | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_2 | LIBFM | Current | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_3 | LICFM | Current | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_4 | VAFM | Voltage | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_5 | VBFM | Voltage | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_6 | VCFM | Voltage | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_7 | 3P_F | Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_8 | 3Q_F | Power | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_9 | DC1 | Battery Voltage | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
AI_10 | FREQ | Frequency | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
BO_1 | RB01 | Target Reset | Communications | DNP 1 |  |  | FALSE | D1 | FALSE
The 411L push buttons and display have been enlarged for better visibility.

## DFR_TESLA 4000-A
DFR ERLPhase Tesla 4000-A Settings & Logic
Relay Specification
Manufacturer | ERL Phase Power Technologies
Model | TESLA 4000-A
Part # | A2-16-0-0-2-60-0-0-0-0-A
Function | Digital Fault Recorder
Front View |  |  |  | Rear View
Relay Classification
Device ID (DID) | Setpoint Class | Logic Class | IP Address (IPADDR)
DFR1 | A | 1 | 172.31.100.122
I/O Summary
I/O | Description
See project schematics.
Settings Table
Setting | Value | Description | Category | Function | Setpoint Class | Logic Class | Float | QuickSet Group | SER
TID | GRVR HL WND | Terminal ID | General | Device |  |  | FALSE |  | FALSE
OUT101 | SV01T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT102 | SV02T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT103 | SV03T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT104 | SV04T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT105 | SV05T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT106 | SV06T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT107 | SV07T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT108 | SV08T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT109 | SV09T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT110 | SV10T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT111 | SV11T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT112 | SV12T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT113 | SV13T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT114 | SV14T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT115 | SV15T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
OUT116 | SV16T | Not Used | Outputs | Output |  |  | FALSE |  | FALSE
EPORT | Y | Port Protocol | Communications | Port F |  |  | FALSE |  | FALSE
SPEED | 19200 | Baud Rate | Communications | Port F |  |  | FALSE |  | FALSE
EPORT | Y | Enable Port | Communications | Port 1 |  |  | FALSE |  | FALSE
ETELNET | Y | Enable Telnet | Communications | Port 1 |  |  | FALSE |  | FALSE
EFTP | Y | Enable FTP | Communications | Port 1 |  |  | FALSE |  | FALSE
EPING | Y | Enable Ping | Communications | Port 1 |  |  | FALSE |  | FALSE
SUBNETM | 255.255.255.0 | Subnet Mask | Communications | Port 1 |  |  | FALSE |  | FALSE
DEFRTR | 172.31.100.254 | Default Router Gateway | Communications | Port 1 |  |  | FALSE |  | FALSE
TPORT | 23 | Telnet Port | Communications | Port 1 |  |  | FALSE |  | FALSE
NETMODE | FAILOVER | Port Operating Mode | Communications | Port 1 |  |  | FALSE |  | FALSE
NETPORT | A | Primary Port | Communications | Port 1 |  |  | FALSE |  | FALSE
EDNP | 1 | Enable DNP Session | Communications | Port 1 |  |  | FALSE |  | FALSE
DNPADR | 1 | DNP Address | Communications | Port 1 |  |  | FALSE |  | FALSE
DNPIP1 | 172.31.100.241 | DNP Client IP | Communications | Port 1 |  |  | FALSE |  | FALSE
DNPNUM1 | 20000 | DNP TCP Port | Communications | Port 1 |  |  | FALSE |  | FALSE
REPADR1 | 0 | Client DNP Address | Communications | Port 1 |  |  | FALSE |  | FALSE
DNPMAP1 | 1 | DNP Map | Communications | Port 1 |  |  | FALSE |  | FALSE
DVARAI1 | 5 | DNP Analog Input Variation | Communications | Port 1 |  |  | FALSE |  | FALSE
BI_00 | ENABLED | Relay Enabled | Communications | DNP |  |  | FALSE |  | FALSE
BI_01 | IRIGOK | IRIG Status | Communications | DNP |  |  | FALSE |  | FALSE
BI_02 | IN201 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_03 | IN202 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_04 | IN203 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_05 | IN204 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_06 | IN205 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_07 | IN206 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_08 | IN207 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_09 | IN208 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_10 | IN209 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_11 | IN210 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_12 | IN211 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_13 | IN212 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_14 | IN213 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_15 | IN214 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_16 | IN215 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_17 | IN216 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_18 | IN301 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_19 | IN302 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_20 | IN303 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_21 | IN304 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_22 | IN305 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_23 | IN306 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_24 | IN307 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_25 | IN308 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_26 | IN309 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_27 | IN310 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_28 | IN311 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_29 | IN312 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_30 | IN313 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_31 | IN314 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_32 | IN315 | I/O | Communications | DNP |  |  | FALSE |  | FALSE
BI_33 | IN316 | I/O | Communications | DNP |  |  | FALSE |  | FALSE